## tblRevisionHistory
keyName	keyValue	Ver	ChangedBy	ChangedDate	ChangeNumber	Description
FS	DI1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	HE1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	MI1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	DI1	2	David Paspa	14-Nov-17	NA	Added something
FS	MOD1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	MOT1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	PC1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	PI1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	PI2	1	David Paspa	13-Nov-17	NA	Initial Design
FS	POS1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	POS2	1	David Paspa	13-Nov-17	NA	Initial Design
FS	POS3	1	David Paspa	13-Nov-17	NA	Initial Design
FS	POS4	1	David Paspa	13-Nov-17	NA	Initial Design
FS	SIC1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	TC1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	TI1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	TI2	1	David Paspa	13-Nov-17	NA	Initial Design
FS	ZSC1	1	David Paspa	13-Nov-17	NA	Initial Design
FS	ZSC2	1	David Paspa	13-Nov-17	NA	Initial Design
FS	ZL	1	David Paspa	13-Nov-17	NA	Initial Design
IO	IO	1	David Paspa	17-Dec-17	NA	Initial Design
Physical	Physical	1	David Paspa	12-Jan-18	NA	Storage Vessel Fabrication Mechanical Items
specificationClass	EM	1	David Paspa	13-Nov-17	NA	Initial Design
specificationClass	EM	2	David Paspa	15-Feb-18	NA	Final EM structure
Physical	Physical	2	David Paspa	6-Mar-18	NA	Mixing Vessel Fabrication Mechanical Items
IO	IO	2	David Paspa	6-Mar-18	NA	Changed POS4 to POS2 or POS3

## tblDocuments
Type	Number	Version	Title
qp	A170810-DS-QLP-SMS-001	A	Quality Plan Solution Manufacturing System
urs			SMS User Requirements Specification
list	A170810-DS-RSP-001	A	Recommended Spare Parts List
test	A170810-QR-TST-001	A	Storage Vessel S1 Factory Acceptance Test
test	A170810-QR-TST-002	A	Storage Vessel S2 Factory Acceptance Test
test	A170810-QR-TST-003	A	Mixing Vessel M1 Factory Acceptance Test
test	A170810-QR-TST-004	A	Mixing Vessel M2 Factory Acceptance Test

## tblTest
Campaign	Title	Date	Tester	Supervisor
TC1	Storage Vessels FAT	22-Feb-18	Chawengsak	David
TC2	Mixing Vessels FAT	6-Mar-18	Chawengsak	David
TC3

## tblInstance
Level	Instance	ID	Class	ClassID	Description	Parent	ParentClass	ParentID	GParent	GParentID	GGParent	GGParentID	GGGParent	GGGParentID	OwnerID	MSClass	MSClassID	P&ID	Serial Number	Prefix	NumInstance	Module	childAliasTag	childAliasClass	childAlias	childSFCAlias	lnk1Tag	lnk1Class	lnk2Tag	lnk2Class	Tubing
CM	AG1101	1	SIC1	27	M1 Agitator	EA1010	EMA1	132	M1	165	PCM1	155	R021	159	132	mAGT	1	A170810-PR-SMS-PID-001		AG	1101	AG_1101	AGn101	SIC1	SIC_AGIT	_sic_agit	MI1101	MI1	EM1009	EMM1	0
CM	BAV1139	2	POS4	26	M1 Vent line drain valve	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133	mBAV1	31	A170810-PR-SMS-PID-001		BAV	1139	BAV_1139	BAVn139	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	DV1101	3	POS2	24	M1 Vent Valve	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133	mDV	5	A170810-PR-SMS-PID-001		DV	1101	DV_1101	DVn101	POS2	POS_VENT	_pos_vent					0
CM	DV1103	4	POS2	24	M1 HP CA Supply Valve	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133	mDV1	6	A170810-PR-SMS-PID-001		DV	1103	DV_1103	DVn103	POS2	POS_HPCA	_pos_hpca					0
CM	DV1105	5	POS2	24	M1 LP CA Supply Valve	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133	mDV1	6	A170810-PR-SMS-PID-001		DV	1105	DV_1105	DVn105	POS2	POS_LPCA	_pos_lpca					0
CM	DV1107	6	POS2	24	M1 Vacuum valve	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133	mDV3	8	A170810-PR-SMS-PID-001		DV	1107	DV_1107	DVn107	POS2	POS_VACUUM	_pos_vacuum					0
CM	PI1103	7	PI1	21	M1 Vessel Pressure	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133	mPT	20	A170810-PR-SMS-PID-001		PI	1103	PI_1103	PIn103	PI1	PI_VESSEL	_pi_vessel					0
CM	PC1103	8	PC1	22	M1 Pressure Control	EC1001	EMC1	133	M1	165	PCM1	155	R021	159	133		0	A170810-PR-SMS-PID-001		PC	1103	PC_1103	PCn103	PC1	PC_VESSEL	_pc_vessel	PI_1103
CM	DV1109	9	POS2	24	M1 PS Supply for WFI Loop	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mDV6	11	A170810-PR-SMS-PID-001		DV	1109	DV_1109	DVn109	POS2	POS_PSWFI	_pos_pswfi					0
CM	DV1111	10	POS4	26	M1 WFI Supply Valve	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mDV5	10	A170810-PR-SMS-PID-001		DV	1111	DV_1111	DVn111	POS4	POS_WFI	_pos_wfi					0
CM	DV1113	11	POS4	26	M1 PW Supply Valve	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mDV5	10	A170810-PR-SMS-PID-001		DV	1113	DV_1113	DVn113	POS4	POS_PW	_pos_pw					0
CM	DV1115	12	POS2	24	M1 PS Supply for PW Loop	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mDV6	11	A170810-PR-SMS-PID-001		DV	1115	DV_1115	DVn115	POS2	POS_PSPW	_pos_pspw					0
CM	ZSC1103	13	ZSC2	32	M1 WFI Supply Flowpath Indicator	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1103	ZSC_1103	ZSCn103	ZSC2	ZSC_FPWFI	_zsc_fpwfi					0
CM	ZSC1105	14	ZSC2	32	M1 PW Supply Flowpath Indicator	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1105	ZSC_1105	ZSCn105	ZSC2	ZSC_FPPW	_zsc_fppw					0
CM	ZSC1107	15	ZSC2	32	M1 inlet line Flowpath Indicator	EC1002	EMC2	134	M1	165	PCM1	155	R021	159	134	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1107	ZSC_1107	ZSCn107	ZSC2	ZSC_FPINLET	_zsc_fpinlet					0
CM	FILT10	16		0	Mx Vacuum Pump Filter and Moisture Trap	M1	MX	165	PCM1	155	R021	159	MPF	164		mFILT5	50	A170810-PR-SMS-PID-004		FILT	10	FILT_10	FILTn0								0
CM	BV1210	17		0	Mx Vacuum Pump 1 Isolation Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mBAV7	61	A170810-PR-SMS-PID-004		BV	1210	BV_1210	BVn210								0
CM	VP1000	18	MOT1	20	Mx Vacuum Pump 1	EC1012	EMC5	135	M1	165	PCM1	155	R021	159	135	mVP	30	A170810-PR-SMS-PID-004		VP	1000	VP_1000	VPn000	MOT1	MOT_PUMP1	_mot_pump1					0
CM	BV1211	19		0	Mx Vacuum Pump 2 Isolation Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mBAV7	61	A170810-PR-SMS-PID-004		BV	1211	BV_1211	BVn211								0
CM	VP1001	20	MOT1	20	Mx Vacuum Pump 2	EC1012	EMC5	135	M1	165	PCM1	155	R021	159	135	mVP	30	A170810-PR-SMS-PID-004		VP	1001	VP_1001	VPn001	MOT1	MOT_PUMP2	_mot_pump2					0
CM	FILT30	21		0	Sy Vacuum Pump Filter and Moisture Trap	S1	SY	171	PCS1	157	R024	161	MPF	164		mFILT5	50	A170810-PR-SMS-PID-004		FILT	30	FILT_30	FILTn0								0
CM	BV3210	22		0	Sy Vacuum Pump 1 Isolation Valve	S1	SY	171	PCS1	157	R024	161	MPF	164		mBAV7	61	A170810-PR-SMS-PID-004		BV	3210	BV_3210	BVn210								0
CM	VP3000	23	MOT1	20	Sy Vacuum Pump 1	EC3012	EMC5	146	S1	171	PCS1	157	R024	161	146	mVP	30	A170810-PR-SMS-PID-004		VP	3000	VP_3000	VPn000	MOT1	MOT_PUMP1	_mot_pump1					0
CM	BV3211	24		0	Sy Vacuum Pump 2 Isolation Valve	S1	SY	171	PCS1	157	R024	161	MPF	164		mBAV7	61	A170810-PR-SMS-PID-004		BV	3211	BV_3211	BVn211								0
CM	VP3001	25	MOT1	20	Sy Vacuum Pump 2	EC3012	EMC5	146	S1	171	PCS1	157	R024	161	146	mVP	30	A170810-PR-SMS-PID-004		VP	3001	VP_3001	VPn001	MOT1	MOT_PUMP2	_mot_pump2					0
CM	BAV3139	26	POS4	26	S1 Vent line drain valve	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144	mBAV1	31	A170810-PR-SMS-PID-003		BAV	3139	BAV_3139	BAVn139	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	DV3101	27	POS2	24	S1 Vent Valve	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144	mDV	5	A170810-PR-SMS-PID-003		DV	3101	DV_3101	DVn101	POS2	POS_VENT	_pos_vent					0
CM	DV3103	28	POS2	24	S1 HP CA Supply Valve	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144	mDV1	6	A170810-PR-SMS-PID-003		DV	3103	DV_3103	DVn103	POS2	POS_HPCA	_pos_hpca					0
CM	DV3105	29	POS2	24	S1 LP CA Supply Valve	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144	mDV1	6	A170810-PR-SMS-PID-003		DV	3105	DV_3105	DVn105	POS2	POS_LPCA	_pos_lpca					0
CM	DV3107	30	POS2	24	S1 Vacuum valve	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144	mDV3	8	A170810-PR-SMS-PID-003		DV	3107	DV_3107	DVn107	POS2	POS_VACUUM	_pos_vacuum					0
CM	PI3103	31	PI1	21	S1 Vessel Pressure	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144	mPT	20	A170810-PR-SMS-PID-003		PI	3103	PI_3103	PIn103	PI1	PI_VESSEL	_pi_vessel					0
CM	PC3103	32	PC1	22	S1 Pressure Controller	EC3001	EMC1	144	S1	171	PCS1	157	R024	161	144		0	A170810-PR-SMS-PID-003		PC	3103	PC_3103	PCn103	PC1	PC_VESSEL	_pc_vessel	PI_3103
CM	DV3109	33	POS2	24	S1 PS Supply for WFI Loop	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mDV6	11	A170810-PR-SMS-PID-003		DV	3109	DV_3109	DVn109	POS2	POS_PSWFI	_pos_pswfi					0
CM	DV3111	34	POS4	26	S1 WFI Supply Valve	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mDV5	10	A170810-PR-SMS-PID-003		DV	3111	DV_3111	DVn111	POS4	POS_WFI	_pos_wfi					0
CM	DV3113	35	POS4	26	S1 PW Supply Valve	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mDV5	10	A170810-PR-SMS-PID-003		DV	3113	DV_3113	DVn113	POS4	POS_PW	_pos_pw					0
CM	DV3115	36	POS2	24	S1 PS Supply for PW Loop	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mDV6	11	A170810-PR-SMS-PID-003		DV	3115	DV_3115	DVn115	POS2	POS_PSPW	_pos_pspw					0
CM	ZSC3103	37	ZSC2	32	S1 WFI Supply Flowpath Indicator	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3103	ZSC_3103	ZSCn103	ZSC2	ZSC_FPWFI	_zsc_fpwfi					0
CM	ZSC3105	38	ZSC2	32	S1 PW Supply Flowpath Indicator	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3105	ZSC_3105	ZSCn105	ZSC2	ZSC_FPPW	_zsc_fppw					0
CM	ZSC3107	39	ZSC2	32	S1 Inlet line Flowpath Indicator	EC3002	EMC3	145	S1	171	PCS1	157	R024	161	145	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3107	ZSC_3107	ZSCn107	ZSC2	ZSC_FPINLET	_zsc_fpinlet					0
CM	BAV1141	40	POS4	26	M1 Vent Filter AF1101 Drain valve	EG1005	EMG1	136	M1	165	PCM1	155	R021	159	136	mBAV1	31	A170810-PR-SMS-PID-001		BAV	1141	BAV_1141	BAVn141	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	HE1101	41	HE1	17	M1 Electric Heating Element	EG1005	EMG1	136	M1	165	PCM1	155	R021	159	136	mHE	13	A170810-PR-SMS-PID-001		HE	1101	HE_1101	HEn101	HE1	HE_FILTER	_he_filter					0
CM	TI1101	42	TI2	30	M1 Vent Filter Temperature Indicator	EG1005	EMG1	136	M1	165	PCM1	155	R021	159	136	mHE	13	A170810-PR-SMS-PID-001		TI	1101	TI_1101	TIn101	TI2	TI_VENT	_ti_vent					0
CM	TI1103	43	TI2	30	M1 Vent Filter top outlet temperature	EG1005	EMG1	136	M1	165	PCM1	155	R021	159	136	mT2	44	A170810-PR-SMS-PID-001		TI	1103	TI_1103	TIn103	TI2	TI_DRAIN	_ti_drain					0
CM	BAV3141	44	POS4	26	S1 Vent Filter AF3101 Drain valve	EG3005	EMG1	147	S1	171	PCS1	157	R024	161	147	mBAV1	31	A170810-PR-SMS-PID-003		BAV	3141	BAV_3141	BAVn141	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	HE3101	45	HE1	17	S1 Electric Heating Element	EG3005	EMG1	147	S1	171	PCS1	157	R024	161	147	mHE	13	A170810-PR-SMS-PID-003		HE	3101	HE_3101	HEn101	HE1	HE_FILTER	_he_filter					0
CM	TI3101	46	TI2	30	S1 Vent Filter Temperature Indicator	EG3005	EMG1	147	S1	171	PCS1	157	R024	161	147	mHE	13	A170810-PR-SMS-PID-003		TI	3101	TI_3101	TIn101	TI2	TI_VENT	_ti_vent					0
CM	TI3103	47	TI2	30	S1 Vent Filter top outlet temperature	EG3005	EMG1	147	S1	171	PCS1	157	R024	161	147	mT2	44	A170810-PR-SMS-PID-003		TI	3103	TI_3103	TIn103	TI2	TI_DRAIN	_ti_drain					0
CM	MI1101	48	MI1	18	M1 Mass Indicator	EM1009	EMM1	137	M1	165	PCM1	155	R021	159	137	mLC	0	A170810-PR-SMS-PID-001		MI	1101	MI_1101	MIn101	MI1	MI_VESSEL	_mi_vessel
CM	ASL1000	49	DI1	15	Instrument Air Switch	ES1013	EMS1	138	M1	165	PCM1	155	R021	159	138	mASL	2	A170810-PR-SMS-PID-001		ASL	1000	ASL_1000	ASLn000	DI1	DI_ASL	_di_asl					0
CM	ASL3000	50	DI1	15	Instrument Air Switch	ES3013	EMS1	148	S1	171	PCS1	157	R024	161	148	mASL	2	A170810-PR-SMS-PID-003		ASL	3000	ASL_3000	ASLn000	DI1	DI_ASL	_di_asl					0
CM	ES1100	51	DI1	15	M1 Emergency Stop mounted on M1 HMI	ES1013	EMS1	138	M1	165	PCM1	155	R021	159	138	mESTOP	38	A170810-PR-SMS-PID-001		ES	1100	ES_1100	ESn100	DI1	DI_ESTOP	_di_estop					0
CM	ES1101	52	DI1	15	M1 Emergency Stop mounted on M1/M2 Shared HMI	ES1013	EMS1	138	M1	165	PCM1	155	R021	159	138	mESTOP	38	A170810-PR-SMS-PID-001		ES	1101	ES_1101	ESn101	DI1	DI_ESTOPDUP	_di_estopdup					0
CM	ES1200	52	DI1	15	M2 Emergency Stop mounted on M2 HMI Feed to M1	ES1013	EMS1	138	M1	165	PCM1	155	R021	159	138	mESTOP	38	A170810-PR-SMS-PID-001		ES	1200	ES_1200	ESn200	DI1	#N/A	#N/A					0
CM	ES1201	52	DI1	15	M2 Emergency Stop mounted on M1/M2 Shared HMI Feed to M1	ES1013	EMS1	138	M1	165	PCM1	155	R021	159	138	mESTOP	38	A170810-PR-SMS-PID-001		ES	1201	ES_1201	ESn201	DI1	#N/A	#N/A					0
CM	ES3100	53	DI1	15	S1 Emergency Stop mounted on S1 HMI	ES3013	EMS1	148	S1	171	PCS1	157	R024	161	148	mESTOP	38	A170810-PR-SMS-PID-003		ES	3100	ES_3100	ESn100	DI1	DI_ESTOP	_di_estop					0
CM	ES3400	53	DI1	15	S2 Emergency Stop mounted on S2 HMI Feed to S1	ES3013	EMS1	148	S1	171	PCS1	157	R024	161	148	mESTOP	38	A170810-PR-SMS-PID-003		ES	3400	ES_3400	ESn400	DI1	#N/A	#N/A					0
CM	BV1151	54	POS1	23	Manufacturing Filtration Line Cooling Water Return Valve	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142	mBV7	40	A170810-PR-SMS-PID-001		BV	1151	BV_1151	BVn151	POS1	POS_SUPPLY	_pos_supply					0
CM	BV1153	55	POS1	23	Manufacturing Filtration Line Cooling Water Supply Valve	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142	mBV7	40	A170810-PR-SMS-PID-001		BV	1153	BV_1153	BVn153	POS1	POS_RETURN	_pos_return					0
CM	BAV1167	56	POS4	26	Manufacturing Filtration Line Cooling Water Supply Drain Valve	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142	mBAV3	33	A170810-PR-SMS-PID-001		BAV	1167	BAV_1167	BAVn167	POS4	POS_SUPPLYDRAIN	_pos_supplydrain					0
CM	BAV1169	57	POS4	26	Manufacturing Filtration Line Cooling Water Return Drain Valve	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142	mBAV3	33	A170810-PR-SMS-PID-001		BAV	1169	BAV_1169	BAVn169	POS4	POS_RETURNDRAIN	_pos_returndrain					0
CM	TCV1157	58	MOD1	19	Manufacturing Filtration Line cooling water supply valve	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142	mCV	4	A170810-PR-SMS-PID-001		TCV	1157	TCV_1157	TCVn157	MOD1	MOD_TCV	_mod_tcv	TC_1109				0
CM	TI1109	59	TI1	29	Manufacturing Filtration Line Inline Heat Exchanger Temperature	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142	mTT1	28	A170810-PR-SMS-PID-001		TI	1109	TI_1109	TIn109	TI1	TI_HEX	_ti_hex					0
CM	TC1109	60	TC1	28	Manufacturing Filtration Line Inline Heat Exchanger Temperature Controller	ET1003	EMT1	142	M1	165	PCM1	155	R021	159	142		0	A170810-PR-SMS-PID-001		TC	1109	TC_1109	TCn109	TC1	TC_HEX	_tc_hex
CM	DV1121	61	POS2	24	M1 Outlet Valve	EV1004	EMV1	139	M1	165	PCM1	155	R021	159	139	mDV4	9	A170810-PR-SMS-PID-001		DV	1121	DV_1121	DVn121	POS2	POS_OUTLET	_pos_outlet					0
CM	RD1101	63	DI1	15	M1 Burst Disc	EV1004	EMV1	139	M1	165	PCM1	155	R021	159	139	mRD	21	A170810-PR-SMS-PID-001		RD	1101	RD_1101	RDn101	DI1	DI_BURST	_di_burst					0
CM	TI1105	64	TI1	29	M1 Temperature Indicator	EV1004	EMV1	139	M1	165	PCM1	155	R021	159	139	mTI	59	A170810-PR-SMS-PID-001		TI	1105	TI_1105	TIn105	TI1	TI_VESSEL	_ti_vessel					0
CM	ZSC1101	65	ZSC1	31	M1 Manway Close Indicator	EV1004	EMV1	139	M1	165	PCM1	155	R021	159	139	mPROX	17	A170810-PR-SMS-PID-001		ZSC	1101	ZSC_1101	ZSCn101	ZSC1	ZSC_MANWAY	_zsc_manway					0
CM	DV1117	66	POS2	24	M1 Spray Ball 1 Valve	EV1008	EMV2	140	M1	165	PCM1	155	R021	159	140	mDV1	6	A170810-PR-SMS-PID-001		DV	1117	DV_1117	DVn117	POS2	POS_SPRAYBALL1	_pos_sprayball1					0
CM	DV1119	67	POS2	24	M1 Spray Ball 2 Valve	EV1008	EMV2	140	M1	165	PCM1	155	R021	159	140	mDV1	6	A170810-PR-SMS-PID-001		DV	1119	DV_1119	DVn119	POS2	POS_SPRAYBALL2	_pos_sprayball2					0
CM	DV3121	68	POS2	24	S1 Outlet Valve	EV3004	EMV1	149	S1	171	PCS1	157	R024	161	149	mDV4	9	A170810-PR-SMS-PID-003		DV	3121	DV_3121	DVn121	POS2	POS_OUTLET	_pos_outlet					0
CM	RD3101	69	DI1	15	S1 Burst Disc	EV3004	EMV1	149	S1	171	PCS1	157	R024	161	149	mRD	21	A170810-PR-SMS-PID-003		RD	3101	RD_3101	RDn101	DI1	DI_BURST	_di_burst					0
CM	TI3105	70	TI1	29	S1 Temperature Indicator	EV3004	EMV1	149	S1	171	PCS1	157	R024	161	149	mTI	59	A170810-PR-SMS-PID-003		TI	3105	TI_3105	TIn105	TI1	TI_VESSEL	_ti_vessel					0
CM	ZSC3101	71	ZSC1	31	S1 Manway Close Indicator	EV3004	EMV1	149	S1	171	PCS1	157	R024	161	149	mPROX	17	A170810-PR-SMS-PID-003		ZSC	3101	ZSC_3101	ZSCn101	ZSC1	ZSC_MANWAY	_zsc_manway					0
CM	DV3117	72	POS2	24	S1 Spray Ball 1 Valve	EV3008	EMV2	150	S1	171	PCS1	157	R024	161	150	mDV1	6	A170810-PR-SMS-PID-003		DV	3117	DV_3117	DVn117	POS2	POS_SPRAYBALL1	_pos_sprayball1					0
CM	DV3119	73	POS2	24	S1 Spray Ball 2 Valve	EV3008	EMV2	150	S1	171	PCS1	157	R024	161	150	mDV1	6	A170810-PR-SMS-PID-003		DV	3119	DV_3119	DVn119	POS2	POS_SPRAYBALL2	_pos_sprayball2					0
CM	BAV1143	74	POS4	26	M1 SIP Condensate Drain Valve	EX1006	EMX4	141	M1	165	PCM1	155	R021	159	141	mBAV4	34	A170810-PR-SMS-PID-001		BAV	1143	BAV_1143	BAVSIP	POS4	POS_SIP	_pos_sip					0
CM	BAV1145	75	POS4	26	M1 CIP Drain Valve	EX1006	EMX4	141	M1	165	PCM1	155	R021	159	141	mBAV5	35	A170810-PR-SMS-PID-001		BAV	1145	BAV_1145	BAVCIP	POS4	POS_CIP	_pos_cip					0
CM	TI1107	76	TI2	30	M1 Drain Temperature Indicator	EX1006	EMX4	141	M1	165	PCM1	155	R021	159	141	mT1	43	A170810-PR-SMS-PID-001		TI	1107	TI_1107	TISIP	TI2	TI_DRAIN	_ti_drain					0
CM	DV1135	77	POS2	24	SMFL1 Filtration Line filter outlet drain valve	EX1015	EMX6	153	SMFL1	167	PCM1	155	R021	159	153	mDV2	7	A170810-PR-SMS-PID-001		DV	1135	DV_1135	DVn135	POS2	POS_DRAIN	_pos_drain					0
CM	DV1137	78	POS2	24	SMFL1 Filtration Line filter outlet valve	EX1015	EMX6	153	SMFL1	167	PCM1	155	R021	159	153	mDV2	7	A170810-PR-SMS-PID-001		DV	1137	DV_1137	DVn137	POS2	POS_FILTER	_pos_filter					0
CM	ZSC1109	79	ZSC2	32	SMFL1 Filtration Line outlet Flowpath Indicator	EX1015	EMX6	153	SMFL1	167	PCM1	155	R021	159	153	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1109	ZSC_1109	ZSCn109	ZSC2	ZSC_FILTER	_zsc_filter					0
CM	ZSC1111	80	ZSC2	32	SMFL1 Filtration Outlet CIP & SIP Flowpath Indicator	EX1015	EMX6	153	SMFL1	167	PCM1	155	R021	159	153	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1111	ZSC_1111	ZSCn111	ZSC2	ZSC_SMFL1	_zsc_smfl1					0
CM	ZSC3111	81	ZSC2	32	VTL1 to M1 Flowpath Indicator	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3111	ZSC_3111	ZSCn111	ZSC2	ZSC_SMFL1	_zsc_smfl1					0
CM	ZSC3113	82	ZSC2	32	VTL1 to M2 Flowpath Indicator	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3113	ZSC_3113	ZSCn113	ZSC2	ZSC_FILTER	_zsc_filter					0
CM	BAV1147	83	POS4	26	SMFL1 Filtration Line SIP Condenste Drain Valve	EX1011	EMX4	154	SMFL1	167	PCM1	155	R021	159	154	mBAV4	34	A170810-PR-SMS-PID-001		BAV	1147	BAV_1147	BAVSIP	POS4	POS_SIP	_pos_sip					0
CM	BAV1149	84	POS4	26	SMFL1 Filtration Line CIP Drain Valve	EX1011	EMX4	154	SMFL1	167	PCM1	155	R021	159	154	mBAV4	34	A170810-PR-SMS-PID-001		BAV	1149	BAV_1149	BAVCIP	POS4	POS_CIP	_pos_cip					0
CM	TI1111	85	TI2	30	SMFL1 Drain Temperature Indicator	EX1011	EMX4	154	SMFL1	167	PCM1	155	R021	159	154	mT	26	A170810-PR-SMS-PID-001		TI	1111	TI_1111	TISIP	TI2	TI_DRAIN	_ti_drain					0
CM	DV1171	86	POS2	24	MMFL1 Filtration Line filter inlet drain valve	EX1014	EMX1	143	M1	165	PCM1	155	R021	159	143	mDV3	8	A170810-PR-SMS-PID-001		DV	1171	DV_1171	DVn171	POS2	POS_FILTERINLET	_pos_filterinlet					0
CM	DV1173	87	POS2	24	MMFL1 Inline Heat Exchanger inlet valve	EX1014	EMX1	143	M1	165	PCM1	155	R021	159	143	mDV3	8	A170810-PR-SMS-PID-001		DV	1173	DV_1173	DVn173	POS2	POS_HEXINLET	_pos_hexinlet					0
CM	ZSC1113	88	ZSC2	32	MMFL1 Filtration Inlet Flowpath Indicator	EX1014	EMX1	143	M1	165	PCM1	155	R021	159	143	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1113	ZSC_1113	ZSCn113	ZSC2	ZSC_FILTER	_zsc_filter					0
CM	ZSC1115	89	ZSC2	32	MMFL1 Filtration Inlet CIP & SIP Flowpath Indicator	EX1014	EMX1	143	M1	165	PCM1	155	R021	159	143	mPROX1	18	A170810-PR-SMS-PID-001		ZSC	1115	ZSC_1115	ZSCn115	ZSC2	ZSC_CIPSIP	_zsc_cipsip					0
CM	BAV3143	90	POS4	26	S1 SIP Drain valve	EX3006	EMX4	151	S1	171	PCS1	157	R024	161	151	mBAV4	34	A170810-PR-SMS-PID-003		BAV	3143	BAV_3143	BAVSIP	POS4	POS_SIP	_pos_sip					0
CM	BAV3145	91	POS4	26	S1 CIP Drain valve	EX3006	EMX4	151	S1	171	PCS1	157	R024	161	151	mBAV5	35	A170810-PR-SMS-PID-003		BAV	3145	BAV_3145	BAVCIP	POS4	POS_CIP	_pos_cip					0
CM	TI3107	92	TI2	30	S1 Drain temperature	EX3006	EMX4	151	S1	171	PCS1	157	R024	161	151	mT1	43	A170810-PR-SMS-PID-003		TI	3107	TI_3107	TISIP	TI2	TI_DRAIN	_ti_drain					0
CM	DV3123	93	POS2	24	S1 Transfer line valve from vessel	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mDV3	8	A170810-PR-SMS-PID-003		DV	3123	DV_3123	DVn123	POS2	POS_VESSEL	_pos_vessel					0
CM	DV3125	94	POS2	24	S1 Transfer line valve from SMFL	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mDV3	8	A170810-PR-SMS-PID-003		DV	3125	DV_3125	DVn125	POS2	POS_SMFL	_pos_smfl					0
CM	DV3127	95	POS2	24	S1 Transfer line valve to drain	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mDV3	8	A170810-PR-SMS-PID-003		DV	3127	DV_3127	DVn127	POS2	POS_DRAIN	_pos_drain					0
CM	DV3129	96	POS2	24	S1 Transfer line valve to filling	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mDV3	8	A170810-PR-SMS-PID-003		DV	3129	DV_3129	DVn129	POS2	POS_FILL	_pos_fill					0
CM	ZSC3115	97	ZSC2	32	S1 to F1P1 Flowpath Indicator	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3115	ZSC_3115	ZSCn115	ZSC2	ZSC_CIPSIP	_zsc_cipsip					0
CM	ZSC3117	98	ZSC2	32	S1 to F2P1 Flowpath Indicator	EX3007	EMX2	152	S1	171	PCS1	157	R024	161	152	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3117	ZSC_3117	ZSCn117	ZSC2	ZSC_BFS2	_zsc_bfs2					0
CM	FILT14	99		0	Mx Compressed Air Source Filter	M1	MX	165	PCM1	155	R021	159	MPF	164		mFILT1	46	A170810-PR-SMS-PID-001		FILT	14	FILT_14	FILTn4								0
CM	FILT11	100		0	MMFL1 Filter Press	M1	MX	165	PCM1	155	R021	159	MPF	164		mFILT2	47	A170810-PR-SMS-PID-001		FILT	11	FILT_11	FILTn1								0
CM	FILT31	101		0	Sy Compressed Air Source Filter	S1	SY	171	PCS1	157	R024	161	MPF	164		mFILT1	46	A170810-PR-SMS-PID-003		FILT	31	FILT_31	FILTn1								0
CM	FILT12	102		0	SMFL1 Pre Filter	SMFL1	SMFL	167	PCM1	155	R021	159	MPF	164		mFILT3	48	A170810-PR-SMS-PID-001		FILT	12	FILT_12	FILTn2								0
CM	FILT13	103		0	SMFL1 Sterile Filter	SMFL1	SMFL	167	PCM1	155	R021	159	MPF	164		mFILT4	49	A170810-PR-SMS-PID-001		FILT	13	FILT_13	FILTn3								0
CM	AF1101	104		0	M1 Vent Filter	M1	MX	165	PCM1	155	R021	159	MPF	164		mFILT	12	A170810-PR-SMS-PID-001		AF	1101	AF_1101	AFn101								0
CM	AF3101	105		0	S1 Vent Filter	S1	SY	171	PCS1	157	R024	161	MPF	164		mFILT	12	A170810-PR-SMS-PID-002		AF	3101	AF_3101	AFn101								0
CM	BAV1101	106		0	M1 filter integrity test compressed air supply valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mBAV6	41	A170810-PR-SMS-PID-001		BAV	1101	BAV_1101	BAVn101								0
CM	BV1159	107		0	M1 Cooling Water Outlet TCV Outlet Isolation Hand Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mBV6	36	A170810-PR-SMS-PID-001		BV	1159	BV_1159	BVn159								0
CM	BV1161	108		0	M1 Cooling Water Outlet TCV Inlet Isolation Hand Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mBV6	36	A170810-PR-SMS-PID-001		BV	1161	BV_1161	BVn161								0
CM	BV1175	109		0	MFL1 Filter Press Inlet Hand Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mDV14	51	A170810-PR-SMS-PID-001		BV	1175	BV_1175	BVn175								0
CM	BV1177	110		0	MFL1 Filter Press Outlet Hand Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mDV14	51	A170810-PR-SMS-PID-001		BV	1177	BV_1177	BVn177								0
CM	GV1165	111		0	M1 Cooling Water Inlet Bypass Hand Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mGV	37	A170810-PR-SMS-PID-001		GV	1165	GV_1165	GVn165								0
CM	LC1101	112		0	M1 Load Cell	M1	MX	165	PCM1	155	R021	159	MPF	164		mLC1	52	A170810-PR-SMS-PID-001		LC	1101	LC_1101	LCn101								0
CM	LC1103	113		0	M1 Load Cell	M1	MX	165	PCM1	155	R021	159	MPF	164		mLC1	52	A170810-PR-SMS-PID-001		LC	1103	LC_1103	LCn103								0
CM	LC1102	114		0	M1 Load Cell	M1	MX	165	PCM1	155	R021	159	MPF	164		mLC1	52	A170810-PR-SMS-PID-001		LC	1102	LC_1102	LCn102								0
CM	PG1101	115		0	M1 Vent Filter Outlet Pressure	M1	MX	165	PCM1	155	R021	159	MPF	164		mPG	16	A170810-PR-SMS-PID-001		PG	1101	PG_1101	PGn101								0
CM	PG3101	116		0	S1 Vent Filter Outlet Pressure	S1	SY	171	PCS1	157	R024	161	MPF	164		mPG	16	A170810-PR-SMS-PID-002		PG	3101	PG_3101	PGn101								0
CM	ST1101	117		0	M1 CA Supply Line Drain Steam Trap	M1	MX	165	PCM1	155	R021	159	MPF	164		mST	25	A170810-PR-SMS-PID-001		ST	1101	ST_1101	STn101								0
CM	ST1103	118		0	M1 Vent Filter Drain Line Steam Trap	M1	MX	165	PCM1	155	R021	159	MPF	164		mST	25	A170810-PR-SMS-PID-001		ST	1103	ST_1103	STn103								0
CM	ST1105	119		0	M1 Outline Line Steam Trap	M1	MX	165	PCM1	155	R021	159	MPF	164		mST	25	A170810-PR-SMS-PID-001		ST	1105	ST_1105	STn105								0
CM	ST1107	120		0	SMFL1 Filtration Line Steam Trap	M1	MX	165	PCM1	155	R021	159	MPF	164		mST	25	A170810-PR-SMS-PID-001		ST	1107	ST_1107	STn107								0
CM	ST3101	121		0	S1 CA Supply Line Drain Steam Trap	S1	SY	171	PCS1	157	R024	161	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	3101	ST_3101	STn101								0
CM	ST3103	122		0	S1 Vent filter drain line steam trap	S1	SY	171	PCS1	157	R024	161	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	3103	ST_3103	STn103								0
CM	ST3105	123		0	S1 Outlet Line steam trap	S1	SY	171	PCS1	157	R024	161	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	3105	ST_3105	STn105								0
CM	XLC1101	124		0	M1 Vessel Light	M1	MX	165	PCM1	155	R021	159	MPF	164		mSG	23	A170810-PR-SMS-PID-001		XLC	1101	XLC_1101	XLCn101								0
CM	XLC3101	125		0	S1 Vessel Light	S1	SY	171	PCS1	157	R024	161	MPF	164		mSG	23	A170810-PR-SMS-PID-002		XLC	3101	XLC_3101	XLCn101								0
CM	XW1117	126		0	M1 Spray Ball 1	M1	MX	165	PCM1	155	R021	159	MPF	164		mSB	22	A170810-PR-SMS-PID-001		XW	1117	XW_1117	XWn117								0
CM	XW1119	127		0	M1 Spray Ball 2	M1	MX	165	PCM1	155	R021	159	MPF	164		mSB	22	A170810-PR-SMS-PID-001		XW	1119	XW_1119	XWn119								0
CM	XW3117	128		0	S1 Spray Ball 1	S1	SY	171	PCS1	157	R024	161	MPF	164		mSB	22	A170810-PR-SMS-PID-002		XW	3117	XW_3117	XWn117								0
CM	XW3119	129		0	S1 Spray Ball 2	S1	SY	171	PCS1	157	R024	161	MPF	164		mSB	22	A170810-PR-SMS-PID-002		XW	3119	XW_3119	XWn119								0
CM	PB74101	130	DI2	16	BFS1 Pause Software Push Button	EX7402	EMX5	131	BFS1	#N/A	#N/A	#N/A	#N/A	#N/A	131		0	A170810-PR-SMS-PID-005		PB	74101	PB_74101	PBn4101	DI2	DI_PAUSE	_di_pause
EM	EX7402	131	EMX5	47	BFS1 Filling Machine	BFS1	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A		0	A170810-PR-SMS-PID-005		EX	7402	EX_7402	EXn402	EMX5	EMX_INLET	_emx_inlet
EM	EA1010	132	EMA1	33	M1 Vessel Agitator	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EA	1010	EA_1010	EAn010	EMA1	EMA_VESSEL	_ema_vessel
EM	EC1001	133	EMC1	34	M1 LP CA and HP CA supply, Vacuum and Vent	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EC	1001	EC_1001	ECn001	EMC1	EMC_GAS	_emc_gas
EM	EC1002	134	EMC2	35	M1 WFI and PS supply plus PW and PS supply	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EC	1002	EC_1002	ECn002	EMC2	EMC_WATER	_emc_water
EM	EC1012	135	EMC5	37	Mixing Vessels Vacuum System	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-004		EC	1012	EC_1012	ECn012	EMC5	EMC_VACUUM	_emc_vacuum
EM	EG1005	136	EMG1	38	M1 gas filter heating, drain valve and temperature indicator	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EG	1005	EG_1005	EGn005	EMG1	EMG_FILTER	_emg_filter
EM	EM1009	137	EMM1	39	M1 load cell	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EM	1009	EM_1009	EMn009	EMM1	EMM_VESSEL	_emm_vessel
EM	ES1013	138	EMS1	40	M1 Emergency Stop	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		ES	1013	ES_1013	ESn013	EMS1	EMS_ESTOP	_ems_estop
EM	EV1004	139	EMV1	42	M1 vessel mounted equipment and valves	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EV	1004	EV_1004	EVn004	EMV1	EMV_VESSEL	_emv_vessel
EM	EV1008	140	EMV2	43	M1 Vessel Inlet Connection	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EV	1008	EV_1008	EVn008	EMV2	EMV_INLET	_emv_inlet
EM	EX1006	141	EMX4	46	M1 CIP & SIP Drain	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EX	1006	EX_1006	EXn006	EMX4	EMX_DRAIN	_emx_drain
EM	ET1003	142	EMT1	41	Manufacturing Filtration Line Heat Exchanger Temperature Control	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		ET	1003	ET_1003	ETn003	EMT1	EMT_HEX	_emt_hex
EM	EX1014	143	EMX1	44	MMFL1 filtration transfer line	M1	MX	165	PCM1	155	R021	159	MPF	164	165		0	A170810-PR-SMS-PID-001		EX	1014	EX_1014	EXn014	EMX1	EMX_MFL	_emx_mfl
EM	EC3001	144	EMC1	34	S1 LP CA and HP CA supply, Vacuum and Vent	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		EC	3001	EC_3001	ECn001	EMC1	EMC_GAS	_emc_gas
EM	EC3002	145	EMC3	36	S1 WFI and PS supply plus PW and PS supply	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		EC	3002	EC_3002	ECn002	EMC3	EMC_WATER	_emc_water
EM	EC3012	146	EMC5	37	Storage Vessels Vacuum System	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-004		EC	3012	EC_3012	ECn012	EMC5	EMC_VACUUM	_emc_vacuum
EM	EG3005	147	EMG1	38	S1 gas filter heating, drain valve and temperature indicator	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		EG	3005	EG_3005	EGn005	EMG1	EMG_FILTER	_emg_filter
EM	ES3013	148	EMS1	40	S1 Emergency Stop	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		ES	3013	ES_3013	ESn013	EMS1	EMS_ESTOP	_ems_estop
EM	EV3004	149	EMV1	42	S1 vessel mounted equipment and valves	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		EV	3004	EV_3004	EVn004	EMV1	EMV_VESSEL	_emv_vessel
EM	EV3008	150	EMV2	43	S1 Vessel Inlet Connection	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		EV	3008	EV_3008	EVn008	EMV2	EMV_INLET	_emv_inlet
EM	EX3006	151	EMX4	46	S1 Vessel CIP & SIP Drain	S1	SY	171	PCS1	157	R024	161	MPF	164	171		0	A170810-PR-SMS-PID-003		EX	3006	EX_3006	EXn006	EMX4	EMX_DRAIN	_emx_drain							_emx4_drain_subs
EM	EX3007	152	EMX2	45	S1 Vessel Transfer Lines	S1	SY	171	PCS1	157	R024	161	MPF	164	0		0	A170810-PR-SMS-PID-003		EX	3007	EX_3007	EXn007	EMX2	EMX_TRANSFER	_emx_transfer
EM	EX1015	153	EMX6	48	SMFL1 filtration transfer line	SMFL1	SMFL	167	PCM1	155	R021	159	MPF	164	0		0	A170810-PR-SMS-PID-001		EX	1015	EX_1015	EXn015	EMX6	EMX_SMFL	_emx_smfl							EMX4_DRAIN_SUBS
EM	EX1011	154	EMX4	46	SMFL1 CIP & SIP Drain Line	SMFL1	SMFL	167	PCM1	155	R021	159	MPF	164	167		0	A170810-PR-SMS-PID-001		EX	1011	EX_1011	EXn011	EMX4	EMX_DRAIN	_emx_drain
PC	PCM1	155	PCSMS	49	Mixing Vessel 1	R021	ROOM	159	MPF	164		0		0	159		0			PCM	1	PCM_1	PCMn	PCSMS	PCMn	_pcmn
PC	PCM2	156	PCSMS	49	Mixing Vessel 2	R022	ROOM	160	MPF	164		0		0	160		0			PCM	2	PCM_2	PCMn	PCSMS	PCMn	_pcmn
PC	PCS1	157	PCSMS	49	Storage Vessel S1	R024	ROOM	161	MPF	164		0		0	161		0			PCS	1	PCS_1	PCSn	PCSMS	PCSn	_pcsn
PC	PCS2	158	PCSMS	49	Storage Vessel S2	R024	ROOM	161	MPF	164		0		0	161		0			PCS	2	PCS_2	PCSn	PCSMS	PCSn	_pcsn
RM	R021	159	ROOM	51	Manufacturing Suite 1	MPF	Site	164		0		0		0	164		0			R	021	R_021	Rn21	ROOM	Rn21	_rn21
RM	R022	160	ROOM	51	Manufacturing Suite 2	MPF	Site	164		0		0		0	164		0			R	022	R_022	Rn22	ROOM	Rn22	_rn22
RM	R024	161	ROOM	51	Storage Vessel Room	MPF	Site	164		0		0		0	164		0			R	024	R_024	Rn24	ROOM	Rn24	_rn24
RM	R029	162	ROOM	51	BFS Filling Line 1	MPF	Site	164		0		0		0	164		0			R	029	R_029	Rn29	ROOM	Rn29	_rn29
RM	R030	163	ROOM	51	BFS Filling Line 2	MPF	Site	164		0		0		0	164		0			R	030	R_030	Rn30	ROOM	Rn30	_rn30
SI	MPF	164	Site	57	MPF Site	0	0	0	0	0	0	0	0	0	0	0	0							Site	0	_0
UN	M1	165	MX	53	Manufacturing Vessel 1	PCM1	PCSMS	155	R021	159	MPF	164		0	155	mMx	57	A170810-PR-SMS-PID-001		M	1	M_1	Mn	MX	Mn	_mn					0
UN	M2	166	MX	53	Manufacturing Vessel 2	PCM2	PCSMS	156	R022	160	MPF	164		0	156	mMx	57	A170810-PR-SMS-PID-002		M	2	M_2	Mn	MX	Mn	_mn					0
UN	SMFL1	167	SMFL	54	Storage Filtration Line 1	PCM1	PCSMS	155	R021	159	MPF	164		0	155		0			SMFL	1	SMFL_1	SMFLn	SMFL	SMFLn	_smfln
UN	SMFL2	168	SMFL	54	Storage Filtration Line 2	PCM2	PCSMS	156	R022	160	MPF	164		0	156		0			SMFL	2	SMFL_2	SMFLn	SMFL	SMFLn	_smfln
UN	VTL1	169	SMFL	54	Vessels Transfer Line 1	PCS1	PCSMS	157	R024	161	MPF	164		0	157		0			VTL	1	VTL_1	VTLn	SMFL	VTLn	_vtln
UN	VTL2	170	SMFL	54	Vessels Transfer Line 2	PCS2	PCSMS	158	R024	161	MPF	164		0	158		0			VTL	2	VTL_2	VTLn	SMFL	VTLn	_vtln
UN	S1	171	SY	55	Storage Vessel 1	PCS1	PCSMS	157	R024	161	MPF	164		0	157	mSy	58	A170810-PR-SMS-PID-003		S	1	S_1	Sn	SY	Sn	_sn					0
UN	S2	172	SY	55	Storage Vessel 2	PCS2	PCSMS	158	R024	161	MPF	164		0	158	mSy	58	A170810-PR-SMS-PID-003		S	2	S_2	Sn	SY	Sn	_sn					0
UN	FL1	173	FLZ	52	BFS Filling Line 1	PCS1	PCSMS	157	R024	161	MPF	164		0	157		0			FL	1	FL_1	FLn	FLZ	FLn	_fln
UN	FL2	174	FLZ	52	BFS Filling Line 2	PCS2	PCSMS	158	R024	161	MPF	164		0	158		0			FL	2	FL_2	FLn	FLZ	FLn	_fln
CM	PRV1101	175		0	M1 HP Compressed Air Pressure Regulating Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mPRV	45	A170810-PR-SMS-PID-001		PRV	1101	PRV_1101	PRVn101								0
CM	PRV1103	176		0	M1 LP Compressed Air Pressure Regulating Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mPRV	45	A170810-PR-SMS-PID-001		PRV	1103	PRV_1103	PRVn103								0
CM	DV1120	177		0	M1 Compressed Air Supply Sanitary Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mDV7	62	A170810-PR-SMS-PID-001		DV	1120	DV_1120	DVn120								0
CM	BAV1121	178		0	M1 Compressed Air Supply Isolation Valve	M1	MX	165	PCM1	155	R021	159	MPF	164		mBAV2	32	A170810-PR-SMS-PID-001		BAV	1121	BAV_1121	BAVn121								0
CM	FXH101	179		0	M1 Flexible Hose PW/WFI Supply	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH	63	A170810-PR-SMS-PID-001		FXH	101	FXH_101	FXHn01								0
CM	FXH102	180		0	M1 Flexible Hose Vent Filter	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH2	65	A170810-PR-SMS-PID-001		FXH	102	FXH_102	FXHn02								0
CM	FXH103	181		0	M1 Flexible Hose Bottom Outlet	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH1	64	A170810-PR-SMS-PID-001		FXH	103	FXH_103	FXHn03								0
CM	FXH104	182		0	M1 Flexible Hose Sterile Filter Outlet	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH2	65	A170810-PR-SMS-PID-001		FXH	104	FXH_104	FXHn04								0
CM	FXH105	183		0	M1 Flexible Hose Filter Press Outlet	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH2	65	A170810-PR-SMS-PID-001		FXH	105	FXH_105	FXHn05								0
CM	FXH106	184		0	M1 Flexible Hose Filter Press Inlet	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH2	65	A170810-PR-SMS-PID-001		FXH	106	FXH_106	FXHn06								0
CM	FXH107	184		0	M1 Flexible Hose Sterile Filter Inlet	M1	MX	165	PCM1	155	R021	159	MPF	164		mFXH2	65	A170810-PR-SMS-PID-001		FXH	107	FXH_107	FXHn07								0
CM	HEX1	185		0	M1 In Line Heat Exchanger	M1	MX	165	PCM1	155	R021	159	MPF	164		mHEX	66	A170810-PR-SMS-PID-001		HEX	1	HEX_1	HEXn								0
CM	LAF101	186		0	M1 Laminar Air Flow	M1	MX	165	PCM1	155	R021	159	MPF	164		mLAF	56	A170810-PR-SMS-PID-001		LAF	101	LAF_101	LAFn01								0
CM	DV3120	187		0	S1 Compressed Air Supply Sanitary Valve	S1	SY	171	PCS1	157	R024	161	MPF	164		mDV7	62	A170810-PR-SMS-PID-003		DV	3120	DV_3120	DVn120								0
CM	BAV3121	188		0	S1 Compressed Air Supply Isolation Valve	S1	SY	171	PCS1	157	R024	161	MPF	164		mBAV2	32	A170810-PR-SMS-PID-003		BAV	3121	BAV_3121	BAVn121								0
CM	PRV3101	189		0	S1 HP Compressed Air Pressure Regulating Valve	S1	SY	171	PCS1	157	R024	161	MPF	164		mPRV	45	A170810-PR-SMS-PID-003		PRV	3101	PRV_3101	PRVn101								0
CM	PRV3102	190		0	S1 LP Compressed Air Pressure Regulating Valve	S1	SY	171	PCS1	157	R024	161	MPF	164		mPRV	45	A170810-PR-SMS-PID-003		PRV	3102	PRV_3102	PRVn102								0
CM	FXH301	191		0	S1 Flexible Hose PW/WFI Supply	S1	SY	171	PCS1	157	R024	161	MPF	164		mFXH	63	A170810-PR-SMS-PID-003		FXH	301	FXH_301	FXHn01								0
CM	FILT21	192		0	MMFL2 Filter Press	M2	MX	166	PCM2	156	R022	160	MPF	164		mFILT2	47	A170810-PR-SMS-PID-002		FILT	21	FILT_21	FILTn1								0
EM	EA2010	193	EMA1	33	M2 Vessel Agitator	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EA	2010	EA_2010	EAn010	EMA1	EMA_VESSEL	_ema_vessel
EM	EC2001	194	EMC1	34	M2 LP CA and HP CA supply, Vacuum and Vent	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EC	2001	EC_2001	ECn001	EMC1	EMC_GAS	_emc_gas
EM	EC2002	195	EMC2	35	M2 WFI and PS supply plus PW and PS supply	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EC	2002	EC_2002	ECn002	EMC2	EMC_WATER	_emc_water
EM	EG2005	196	EMG1	38	M2 gas filter heating, drain valve and temperature indicator	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EG	2005	EG_2005	EGn005	EMG1	EMG_FILTER	_emg_filter
EM	EM2009	197	EMM1	39	M2 load cell	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EM	2009	EM_2009	EMn009	EMM1	EMM_VESSEL	_emm_vessel
EM	ES2013	198	EMS1	40	M2 Emergency Stop	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		ES	2013	ES_2013	ESn013	EMS1	EMS_ESTOP	_ems_estop
EM	EV2004	199	EMV1	42	M2 vessel mounted equipment and valves	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EV	2004	EV_2004	EVn004	EMV1	EMV_VESSEL	_emv_vessel
EM	EV2008	200	EMV2	43	M2 Vessel Inlet Connection	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EV	2008	EV_2008	EVn008	EMV2	EMV_INLET	_emv_inlet
EM	EX2006	201	EMX4	46	M2 CIP & SIP Drain	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EX	2006	EX_2006	EXn006	EMX4	EMX_DRAIN	_emx_drain
EM	ET2003	202	EMT1	41	Manufacturing Filtration Line Heat Exchanger Temperature Control	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		ET	2003	ET_2003	ETn003	EMT1	EMT_HEX	_emt_hex
EM	EX2014	203	EMX1	44	MMFL2 filtration transfer line	M2	MX	166	PCM2	156	R022	160	MPF	164	166		0	A170810-PR-SMS-PID-002		EX	2014	EX_2014	EXn014	EMX1	EMX_MFL	_emx_mfl
CM	PRV2101	204		0	M2 HP Compressed Air Pressure Regulating Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mPRV	45	A170810-PR-SMS-PID-002		PRV	2101	PRV_2101	PRVn101								0
CM	PRV2103	205		0	M2 LP Compressed Air Pressure Regulating Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mPRV	45	A170810-PR-SMS-PID-002		PRV	2103	PRV_2103	PRVn103								0
CM	FXH202	206		0	M2 Flexible Hose Vent Filter	M2	MX	166	PCM2	156	R022	160	MPF	164		mFXH2	65	A170810-PR-SMS-PID-002		FXH	202	FXH_202	FXHn02								0
CM	FXH203	207		0	M2 Flexible Hose Bottom Outlet	M2	MX	166	PCM2	156	R022	160	MPF	164		mFXH1	64	A170810-PR-SMS-PID-002		FXH	203	FXH_203	FXHn03								0
CM	FXH204	208		0	M2 Flexible Hose Sterile Filter Outlet	M2	MX	166	PCM2	156	R022	160	MPF	164		mFXH2	65	A170810-PR-SMS-PID-002		FXH	204	FXH_204	FXHn04								0
CM	FXH205	209		0	M2 Flexible Hose Filter Press Outlet	M2	MX	166	PCM2	156	R022	160	MPF	164		mFXH2	65	A170810-PR-SMS-PID-002		FXH	205	FXH_205	FXHn05								0
CM	FXH206	210		0	M2 Flexible Hose Filter Press Inlet	M2	MX	166	PCM2	156	R022	160	MPF	164		mFXH2	65	A170810-PR-SMS-PID-002		FXH	206	FXH_206	FXHn06								0
CM	FXH207	184		0	M2 Flexible Hose Sterile Filter Inlet	M2	MX	166	PCM2	156	R022	160	MPF	164		mFXH2	65	A170810-PR-SMS-PID-001		FXH	207	FXH_207	FXHn07								0
CM	HEX2	211		0	M2 In Line Heat Exchanger	M2	MX	166	PCM2	156	R022	160	MPF	164		mHEX	66	A170810-PR-SMS-PID-002		HEX	2	HEX_2	HEXn								0
CM	LAF201	212		0	M2 Laminar Air Flow	M2	MX	166	PCM2	156	R022	160	MPF	164		mLAF	56	A170810-PR-SMS-PID-002		LAF	201	LAF_201	LAFn01								0
CM	AG2101	213	SIC1	22	M2 Agitator	EA2010	EMA1	193	M2	166	PCM2	156	R022	160	193	mAGT	1	A170810-PR-SMS-PID-002		AG	2101	AG_2101	AGn101	SIC1	SIC_AGIT	_sic_agit	MI2101	MI2	EM2009	EMM1	0
CM	BAV2139	214	POS4	21	M2 Vent line drain valve	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194	mBAV1	31	A170810-PR-SMS-PID-002		BAV	2139	BAV_2139	BAVn139	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	DV2101	215	POS2	21	M2 Vent Valve	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194	mDV	5	A170810-PR-SMS-PID-002		DV	2101	DV_2101	DVn101	POS2	POS_VENT	_pos_vent					0
CM	DV2103	216	POS2	21	M2 HP CA Supply Valve	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194	mDV1	6	A170810-PR-SMS-PID-002		DV	2103	DV_2103	DVn103	POS2	POS_HPCA	_pos_hpca					0
CM	DV2105	217	POS2	21	M2 LP CA Supply Valve	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194	mDV1	6	A170810-PR-SMS-PID-002		DV	2105	DV_2105	DVn105	POS2	POS_LPCA	_pos_lpca					0
CM	DV2107	218	POS2	21	M2 Vacuum valve	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194	mDV3	8	A170810-PR-SMS-PID-002		DV	2107	DV_2107	DVn107	POS2	POS_VACUUM	_pos_vacuum					0
CM	PI2103	219	PI1	18	M2 Vessel Pressure	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194	mPT	20	A170810-PR-SMS-PID-002		PI	2103	PI_2103	PIn103	PI1	PI_VESSEL	_pi_vessel					0
CM	PC2103	220	PC1	19	M2 Pressure Control	EC2001	EMC1	194	M2	166	PCM2	156	R022	160	194		0	A170810-PR-SMS-PID-002		PC	2103	PC_2103	PCn103	PC1	PC_VESSEL	_pc_vessel	PI_2103
CM	DV2109	221	POS2	21	M2 PS Supply for WFI Loop	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mDV6	11	A170810-PR-SMS-PID-002		DV	2109	DV_2109	DVn109	POS2	POS_PSWFI	_pos_pswfi					0
CM	DV2111	222	POS4	21	M2 WFI Supply Valve	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mDV5	10	A170810-PR-SMS-PID-002		DV	2111	DV_2111	DVn111	POS4	POS_WFI	_pos_wfi					0
CM	DV2113	223	POS4	21	M2 PW Supply Valve	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mDV5	10	A170810-PR-SMS-PID-002		DV	2113	DV_2113	DVn113	POS4	POS_PW	_pos_pw					0
CM	DV2115	224	POS2	21	M2 PS Supply for PW Loop	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mDV6	11	A170810-PR-SMS-PID-002		DV	2115	DV_2115	DVn115	POS2	POS_PSPW	_pos_pspw					0
CM	ZSC2103	225	ZSC2	27	M2 WFI Supply Flowpath Indicator	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2103	ZSC_2103	ZSCn103	ZSC2	ZSC_FPWFI	_zsc_fpwfi					0
CM	ZSC2105	226	ZSC2	27	M2 PW Supply Flowpath Indicator	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2105	ZSC_2105	ZSCn105	ZSC2	ZSC_FPPW	_zsc_fppw					0
CM	ZSC2107	227	ZSC2	27	M2 inlet line Flowpath Indicator	EC2002	EMC2	195	M2	166	PCM2	156	R022	160	195	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2107	ZSC_2107	ZSCn107	ZSC2	ZSC_FPINLET	_zsc_fpinlet					0
CM	BAV2141	228	POS4	21	M2 Vent Filter AF1101 Drain valve	EG2005	EMG1	196	M2	166	PCM2	156	R022	160	196	mBAV1	31	A170810-PR-SMS-PID-002		BAV	2141	BAV_2141	BAVn141	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	HE2101	229	HE1	14	M2 Electric Heating Element	EG2005	EMG1	196	M2	166	PCM2	156	R022	160	196	mHE	13	A170810-PR-SMS-PID-002		HE	2101	HE_2101	HEn101	HE1	HE_FILTER	_he_filter					0
CM	TI2101	230	TI2	25	M2 Vent Filter Temperature Indicator	EG2005	EMG1	196	M2	166	PCM2	156	R022	160	196	mHE	13	A170810-PR-SMS-PID-002		TI	2101	TI_2101	TIn101	TI2	TI_VENT	_ti_vent					0
CM	TI2103	231	TI2	25	M2 Vent Filter top outlet temperature	EG2005	EMG1	196	M2	166	PCM2	156	R022	160	196	mT2	44	A170810-PR-SMS-PID-002		TI	2103	TI_2103	TIn103	TI2	TI_DRAIN	_ti_drain					0
CM	MI2101	232	MI1	15	M2 Mass Indicator	EM2009	EMM1	197	M2	166	PCM2	156	R022	160	197	mLC	0	A170810-PR-SMS-PID-002		MI	2101	MI_2101	MIn101	MI1	MI_VESSEL	_mi_vessel
CM	ASL2000	233	DI1	13	Instrument Air Switch	ES2013	EMS1	198	M2	166	PCM2	156	R022	160	198	mASL	2	A170810-PR-SMS-PID-002		ASL	2000	ASL_2000	ASLn000	DI1	DI_ASL	_di_asl					0
CM	ES2100	234	DI1	13	M2 Emergency Stop mounted on M2 HMI	ES2013	EMS1	198	M2	166	PCM2	156	R022	160	198	mESTOP1	39	A170810-PR-SMS-PID-002		ES	2100	ES_2100	ESn100	DI1	DI_ESTOP	_di_estop					0
CM	ES2101	235	DI1	13	M2 Emergency Stop mounted on M1/M2 Shared HMI	ES2013	EMS1	198	M2	166	PCM2	156	R022	160	198	mESTOP1	39	A170810-PR-SMS-PID-002		ES	2101	ES_2101	ESn101	DI1	DI_ESTOPDUP	_di_estopdup					0
CM	BV2151	236	POS1	20	Manufacturing Filtration Line Cooling Water Return Valve	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202	mBV7	40	A170810-PR-SMS-PID-002		BV	2151	BV_2151	BVn151	POS1	POS_SUPPLY	_pos_supply					0
CM	BV2153	237	POS1	20	Manufacturing Filtration Line Cooling Water Supply Valve	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202	mBV7	40	A170810-PR-SMS-PID-002		BV	2153	BV_2153	BVn153	POS1	POS_RETURN	_pos_return					0
CM	BAV2167	238	POS4	21	Manufacturing Filtration Line Cooling Water Supply Drain Valve	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202	mBAV3	33	A170810-PR-SMS-PID-002		BAV	2167	BAV_2167	BAVn167	POS4	POS_SUPPLYDRAIN	_pos_supplydrain					0
CM	BAV2169	239	POS4	21	Manufacturing Filtration Line Cooling Water Return Drain Valve	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202	mBAV3	33	A170810-PR-SMS-PID-002		BAV	2169	BAV_2169	BAVn169	POS4	POS_RETURNDRAIN	_pos_returndrain					0
CM	TCV2157	240	MOD1	16	Manufacturing Filtration Line cooling water supply valve	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202	mCV	4	A170810-PR-SMS-PID-002		TCV	2157	TCV_2157	TCVn157	MOD1	MOD_TCV	_mod_tcv	TC_2109				0
CM	TI2109	241	TI1	24	Manufacturing Filtration Line Inline Heat Exchanger Temperature	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202	mTT1	28	A170810-PR-SMS-PID-002		TI	2109	TI_2109	TIn109	TI1	TI_HEX	_ti_hex					0
CM	TC2109	242	TC1	23	Manufacturing Filtration Line Inline Heat Exchanger Temperature Controller	ET2003	EMT1	202	M2	166	PCM2	156	R022	160	202		0	A170810-PR-SMS-PID-002		TC	2109	TC_2109	TCn109	TC1	TC_HEX	_tc_hex
CM	DV2121	243	POS2	21	M2 Outlet Valve	EV2004	EMV1	199	M2	166	PCM2	156	R022	160	199	mDV4	9	A170810-PR-SMS-PID-002		DV	2121	DV_2121	DVn121	POS2	POS_OUTLET	_pos_outlet					0
CM	RD2101	245	DI1	13	M2 Burst Disc	EV2004	EMV1	199	M2	166	PCM2	156	R022	160	199	mRD	21	A170810-PR-SMS-PID-002		RD	2101	RD_2101	RDn101	DI1	DI_BURST	_di_burst					0
CM	TI2105	246	TI1	24	M2 Temperature Indicator	EV2004	EMV1	199	M2	166	PCM2	156	R022	160	199	mTI	59	A170810-PR-SMS-PID-002		TI	2105	TI_2105	TIn105	TI1	TI_VESSEL	_ti_vessel					0
CM	ZSC2101	247	ZSC1	26	M2 Manway Close Indicator	EV2004	EMV1	199	M2	166	PCM2	156	R022	160	199	mPROX	17	A170810-PR-SMS-PID-002		ZSC	2101	ZSC_2101	ZSCn101	ZSC1	ZSC_MANWAY	_zsc_manway					0
CM	DV2117	248	POS2	21	M2 Spray Ball 1 Valve	EV2008	EMV2	200	M2	166	PCM2	156	R022	160	200	mDV1	6	A170810-PR-SMS-PID-002		DV	2117	DV_2117	DVn117	POS2	POS_SPRAYBALL1	_pos_sprayball1					0
CM	DV2119	249	POS2	21	M2 Spray Ball 2 Valve	EV2008	EMV2	200	M2	166	PCM2	156	R022	160	200	mDV1	6	A170810-PR-SMS-PID-002		DV	2119	DV_2119	DVn119	POS2	POS_SPRAYBALL2	_pos_sprayball2					0
CM	BAV2143	250	POS4	21	M2 SIP Condensate Drain Valve	EX2006	EMX4	201	M2	166	PCM2	156	R022	160	201	mBAV4	34	A170810-PR-SMS-PID-002		BAV	2143	BAV_2143	BAVSIP	POS4	POS_SIP	_pos_sip					0
CM	BAV2145	251	POS4	21	M2 CIP Drain Valve	EX2006	EMX4	201	M2	166	PCM2	156	R022	160	201	mBAV5	35	A170810-PR-SMS-PID-002		BAV	2145	BAV_2145	BAVCIP	POS4	POS_CIP	_pos_cip					0
CM	TI2107	252	TI2	25	M2 Drain Temperature Indicator	EX2006	EMX4	201	M2	166	PCM2	156	R022	160	201	mT1	43	A170810-PR-SMS-PID-002		TI	2107	TI_2107	TISIP	TI2	TI_DRAIN	_ti_drain					0
CM	DV2171	253	POS2	21	MMFL2 Filtration Line filter inlet drain valve	EX2014	EMX1	203	M2	166	PCM2	156	R022	160	203	mDV3	8	A170810-PR-SMS-PID-002		DV	2171	DV_2171	DVn171	POS2	POS_FILTERINLET	_pos_filterinlet					0
CM	DV2173	254	POS2	21	MMFL2 Inline Heat Exchanger inlet valve	EX2014	EMX1	203	M2	166	PCM2	156	R022	160	203	mDV3	8	A170810-PR-SMS-PID-002		DV	2173	DV_2173	DVn173	POS2	POS_HEXINLET	_pos_hexinlet					0
CM	ZSC2113	255	ZSC2	27	MMFL2 Filtration Inlet Flowpath Indicator	EX2014	EMX1	203	M2	166	PCM2	156	R022	160	203	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2113	ZSC_2113	ZSCn113	ZSC2	ZSC_FILTER	_zsc_filter					0
CM	ZSC2115	256	ZSC2	27	MMFL2 Filtration Inlet CIP & SIP Flowpath Indicator	EX2014	EMX1	203	M2	166	PCM2	156	R022	160	203	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2115	ZSC_2115	ZSCn115	ZSC2	ZSC_CIPSIP	_zsc_cipsip					0
EM	EC4001	257	EMC1	30	S2 LP CA and HP CA supply, Vacuum and Vent	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		EC	4001	EC_4001	ECn001	EMC1	EMC_GAS	_emc_gas
EM	EC4002	258	EMC3	32	S2 WFI and PS supply plus PW and PS supply	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		EC	4002	EC_4002	ECn002	EMC3	EMC_WATER	_emc_water
EM	EG4005	259	EMG1	34	S2 gas filter heating, drain valve and temperature indicator	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		EG	4005	EG_4005	EGn005	EMG1	EMG_FILTER	_emg_filter
EM	ES4013	260	EMS1	36	S2 Emergency Stop	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		ES	4013	ES_4013	ESn013	EMS1	EMS_ESTOP	_ems_estop
EM	EV4004	261	EMV1	38	S2 vessel mounted equipment and valves	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		EV	4004	EV_4004	EVn004	EMV1	EMV_VESSEL	_emv_vessel
EM	EV4008	262	EMV2	39	S2 Vessel Inlet Connection	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		EV	4008	EV_4008	EVn008	EMV2	EMV_INLET	_emv_inlet
EM	EX4006	263	EMX4	42	S2 Vessel CIP & SIP Drain	S2	SY	172	PCS2	158	R024	161	MPF	164	172		0	A170810-PR-SMS-PID-003		EX	4006	EX_4006	EXn006	EMX4	EMX_DRAIN	_emx_drain
CM	BAV4139	264	POS4	21	S2 Vent line drain valve	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257	mBAV1	31	A170810-PR-SMS-PID-003		BAV	4139	BAV_4139	BAVn139	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	DV4101	265	POS2	21	S2 Vent Valve	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257	mDV	5	A170810-PR-SMS-PID-003		DV	4101	DV_4101	DVn101	POS2	POS_VENT	_pos_vent					0
CM	DV4103	266	POS2	21	S2 HP CA Supply Valve	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257	mDV1	6	A170810-PR-SMS-PID-003		DV	4103	DV_4103	DVn103	POS2	POS_HPCA	_pos_hpca					0
CM	DV4105	267	POS2	21	S2 LP CA Supply Valve	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257	mDV1	6	A170810-PR-SMS-PID-003		DV	4105	DV_4105	DVn105	POS2	POS_LPCA	_pos_lpca					0
CM	DV4107	268	POS2	21	S2 Vacuum valve	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257	mDV3	8	A170810-PR-SMS-PID-003		DV	4107	DV_4107	DVn107	POS2	POS_VACUUM	_pos_vacuum					0
CM	PI4103	269	PI1	18	S2 Vessel Pressure	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257	mPT	20	A170810-PR-SMS-PID-003		PI	4103	PI_4103	PIn103	PI1	PI_VESSEL	_pi_vessel					0
CM	PC4103	270	PC1	19	S2 Pressure Controller	EC4001	EMC1	257	S2	172	PCS2	158	R024	161	257		0	A170810-PR-SMS-PID-003		PC	4103	PC_4103	PCn103	PC1	PC_VESSEL	_pc_vessel	PI_3103
CM	DV4109	271	POS2	21	S2 PS Supply for WFI Loop	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mDV6	11	A170810-PR-SMS-PID-003		DV	4109	DV_4109	DVn109	POS2	POS_PSWFI	_pos_pswfi					0
CM	DV4111	272	POS4	21	S2 WFI Supply Valve	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mDV5	10	A170810-PR-SMS-PID-003		DV	4111	DV_4111	DVn111	POS4	POS_WFI	_pos_wfi					0
CM	DV4113	273	POS4	21	S2 PW Supply Valve	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mDV5	10	A170810-PR-SMS-PID-003		DV	4113	DV_4113	DVn113	POS4	POS_PW	_pos_pw					0
CM	DV4115	274	POS2	21	S2 PS Supply for PW Loop	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mDV6	11	A170810-PR-SMS-PID-003		DV	4115	DV_4115	DVn115	POS2	POS_PSPW	_pos_pspw					0
CM	ZSC4103	275	ZSC2	27	S2 WFI Supply Flowpath Indicator	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	4103	ZSC_4103	ZSCn103	ZSC2	ZSC_FPWFI	_zsc_fpwfi					0
CM	ZSC4105	276	ZSC2	27	S2 PW Supply Flowpath Indicator	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	4105	ZSC_4105	ZSCn105	ZSC2	ZSC_FPPW	_zsc_fppw					0
CM	ZSC4107	277	ZSC2	27	S2 Inlet line Flowpath Indicator	EC4002	EMC3	258	S2	172	PCS2	158	R024	161	258	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	4107	ZSC_4107	ZSCn107	ZSC2	ZSC_FPINLET	_zsc_fpinlet					0
CM	BAV4141	278	POS4	21	S2 Vent Filter AF3101 Drain valve	EG4005	EMG1	259	S2	172	PCS2	158	R024	161	259	mBAV1	31	A170810-PR-SMS-PID-003		BAV	4141	BAV_4141	BAVn141	POS4	POS_VENTDRAIN	_pos_ventdrain					0
CM	HE4101	279	HE1	14	S2 Electric Heating Element	EG4005	EMG1	259	S2	172	PCS2	158	R024	161	259	mHE	13	A170810-PR-SMS-PID-003		HE	4101	HE_4101	HEn101	HE1	HE_FILTER	_he_filter					0
CM	TI4101	280	TI2	25	S2 Vent Filter Temperature Indicator	EG4005	EMG1	259	S2	172	PCS2	158	R024	161	259	mHE	13	A170810-PR-SMS-PID-003		TI	4101	TI_4101	TIn101	TI2	TI_VENT	_ti_vent					0
CM	TI4103	281	TI2	25	S2 Vent Filter top outlet temperature	EG4005	EMG1	259	S2	172	PCS2	158	R024	161	259	mT2	44	A170810-PR-SMS-PID-003		TI	4103	TI_4103	TIn103	TI2	TI_DRAIN	_ti_drain					0
CM	ASL4000	282	DI1	13	Instrument Air Switch	ES4013	EMS1	260	S2	172	PCS2	158	R024	161	260	mASL	2	A170810-PR-SMS-PID-003		ASL	4000	ASL_4000	ASLn000	DI1	DI_ASL	_di_asl					0
CM	ES4100	283	DI1	13	S2 Emergency Stop mounted on S2 HMI	ES4013	EMS1	260	S2	172	PCS2	158	R024	161	260	mESTOP1	39	A170810-PR-SMS-PID-003		ES	4100	ES_4100	ESn100	DI1	DI_ESTOP	_di_estop					0
CM	DV4121	284	POS2	21	S2 Outlet Valve	EV4004	EMV1	261	S2	172	PCS2	158	R024	161	261	mDV4	9	A170810-PR-SMS-PID-003		DV	4121	DV_4121	DVn121	POS2	POS_OUTLET	_pos_outlet					0
CM	RD4101	285	DI1	13	S2 Burst Disc	EV4004	EMV1	261	S2	172	PCS2	158	R024	161	261	mRD	21	A170810-PR-SMS-PID-003		RD	4101	RD_4101	RDn101	DI1	DI_BURST	_di_burst					0
CM	TI4105	286	TI1	24	S2 Temperature Indicator	EV4004	EMV1	261	S2	172	PCS2	158	R024	161	261	mTI	59	A170810-PR-SMS-PID-003		TI	4105	TI_4105	TIn105	TI1	TI_VESSEL	_ti_vessel					0
CM	ZSC4101	287	ZSC1	26	S2 Manway Close Indicator	EV4004	EMV1	261	S2	172	PCS2	158	R024	161	261	mPROX	17	A170810-PR-SMS-PID-003		ZSC	4101	ZSC_4101	ZSCn101	ZSC1	ZSC_MANWAY	_zsc_manway					0
CM	DV4117	288	POS2	21	S2 Spray Ball 1 Valve	EV4008	EMV2	262	S2	172	PCS2	158	R024	161	262	mDV1	6	A170810-PR-SMS-PID-003		DV	4117	DV_4117	DVn117	POS2	POS_SPRAYBALL1	_pos_sprayball1					0
CM	DV4119	289	POS2	21	S2 Spray Ball 2 Valve	EV4008	EMV2	262	S2	172	PCS2	158	R024	161	262	mDV1	6	A170810-PR-SMS-PID-003		DV	4119	DV_4119	DVn119	POS2	POS_SPRAYBALL2	_pos_sprayball2					0
CM	BAV4143	290	POS4	21	S2 SIP Drain valve	EX4006	EMX4	263	S2	172	PCS2	158	R024	161	263	mBAV4	34	A170810-PR-SMS-PID-003		BAV	4143	BAV_4143	BAVSIP	POS4	POS_SIP	_pos_sip					0
CM	BAV4145	291	POS4	21	S2 CIP Drain valve	EX4006	EMX4	263	S2	172	PCS2	158	R024	161	263	mBAV5	35	A170810-PR-SMS-PID-003		BAV	4145	BAV_4145	BAVCIP	POS4	POS_CIP	_pos_cip					0
CM	TI4107	292	TI2	25	S2 Drain temperature	EX4006	EMX4	263	S2	172	PCS2	158	R024	161	263	mT1	43	A170810-PR-SMS-PID-003		TI	4107	TI_4107	TISIP	TI2	TI_DRAIN	_ti_drain					0
CM	PB84101	293	DI2	16	BFS2 Pause Software Push Button	EX8402	EMX5	294	BFS2	#N/A	#N/A	#N/A	#N/A	#N/A	294		0	A170810-PR-SMS-PID-006		PB	84101	PB_84101	PBn4101	DI2	DI_PAUSE	_di_pause
EM	EX8402	294	EMX5	47	BFS2 Filling Machine	BFS2	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A	#N/A		0	A170810-PR-SMS-PID-006		EX	8402	EX_8402	EXn402	EMX5	EMX_INLET	_emx_inlet
CM	DV2135	295	POS2	21	SMFL2 Filtration Line filter outlet drain valve	EX2015	EMX6	304	SMFL2	168	PCM2	156	R022	160	304	mDV2	7	A170810-PR-SMS-PID-002		DV	2135	DV_2135	DVn135	POS2	POS_DRAIN	_pos_drain					0
CM	DV2137	296	POS2	21	SMFL2 Filtration Line filter outlet valve	EX2015	EMX6	304	SMFL2	168	PCM2	156	R022	160	304	mDV2	7	A170810-PR-SMS-PID-002		DV	2137	DV_2137	DVn137	POS2	POS_FILTER	_pos_filter					0
CM	ZSC2109	297	ZSC2	27	SMFL2 Filtration Line outlet Flowpath Indicator	EX2015	EMX6	304	SMFL2	168	PCM2	156	R022	160	304	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2109	ZSC_2109	ZSCn109	ZSC2	ZSC_FILTER	_zsc_filter					0
CM	ZSC2111	298	ZSC2	27	SMFL2 Filtration Outlet CIP & SIP Flowpath Indicator	EX2015	EMX6	304	SMFL2	168	PCM2	156	R022	160	304	mPROX1	18	A170810-PR-SMS-PID-002		ZSC	2111	ZSC_2111	ZSCn111	ZSC2	ZSC_SMFL1	_zsc_smfl1					0
CM	BAV2147	299	POS4	21	SMFL2 Filtration Line SIP Condenste Drain Valve	EX2011	EMX4	305	SMFL2	168	PCM2	156	R022	160	305	mBAV4	31	A170810-PR-SMS-PID-002		BAV	2147	BAV_2147	BAVSIP	POS4	POS_SIP	_pos_sip					0
CM	BAV2149	300	POS4	21	SMFL2 Filtration Line CIP Drain Valve	EX2011	EMX4	305	SMFL2	168	PCM2	156	R022	160	305	mBAV4	34	A170810-PR-SMS-PID-002		BAV	2149	BAV_2149	BAVCIP	POS4	POS_CIP	_pos_cip					0
CM	TI2111	301	TI2	25	SMFL2 Drain Temperature Indicator	EX2011	EMX4	305	SMFL2	168	PCM2	156	R022	160	305	mT	26	A170810-PR-SMS-PID-002		TI	2111	TI_2111	TISIP	TI2	TI_DRAIN	_ti_drain					0
CM	FILT22	302		0	SMFL2 Pre Filter	SMFL2	SMFL	168	PCM2	156	R022	160	MPF	164		mFILT3	48	A170810-PR-SMS-PID-002		FILT	22	FILT_22	FILTn2								0
CM	FILT23	303		0	SMFL2 Sterile Filter	SMFL2	SMFL	168	PCM2	156	R022	160	MPF	164		mFILT4	49	A170810-PR-SMS-PID-002		FILT	23	FILT_23	FILTn3								0
EM	EX2015	304	EMX6	44	SMFL2 filtration transfer line	SMFL2	SMFL	168	PCM2	156	R022	160	MPF	164	0		0	A170810-PR-SMS-PID-002		EX	2015	EX_2015	EXn015	EMX6	EMX_SMFL	_emx_smfl
EM	EX2011	305	EMX4	42	SMFL2 CIP & SIP Drain Line	SMFL2	SMFL	168	PCM2	156	R022	160	MPF	164	168		0	A170810-PR-SMS-PID-002		EX	2011	EX_2011	EXn011	EMX4	EMX_DRAIN	_emx_drain
EM	EX4007	306	EMX2	45	S2 Vessel Transfer Lines	S2	SY	172	PCS2	158	R024	161	MPF	164	0		0	A170810-PR-SMS-PID-003		EX	4007	EX_4007	EXn007	EMX2	EMX_TRANSFER	_emx_transfer
CM	AF2101	307		0	M2 Vent Filter	M2	MX	166	PCM2	156	R022	160	MPF	164		mFILT	12	A170810-PR-SMS-PID-002		AF	2101	AF_2101	AFn101								0
CM	AF4101	308		0	S2 Vent Filter	S2	SY	172	PCS2	158	R024	161	MPF	164		mFILT	12	A170810-PR-SMS-PID-003		AF	4101	AF_4101	AFn101								0
CM	BAV2101	309		0	M2 filter integrity test compressed air supply valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mBAV6	41	A170810-PR-SMS-PID-002		BAV	2101	BAV_2101	BAVn101								0
CM	BV2159	310		0	M2 Cooling Water Outlet TCV Outlet Isolation Hand Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mBV6	36	A170810-PR-SMS-PID-002		BV	2159	BV_2159	BVn159								0
CM	BV2161	311		0	M2 Cooling Water Outlet TCV Inlet Isolation Hand Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mBV6	36	A170810-PR-SMS-PID-002		BV	2161	BV_2161	BVn161								0
CM	BV2175	312		0	MFL2 Filter Press Inlet Hand Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mDV14	51	A170810-PR-SMS-PID-002		BV	2175	BV_2175	BVn175								0
CM	BV2177	313		0	MFL2 Filter Press Outlet Hand Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mDV14	51	A170810-PR-SMS-PID-002		BV	2177	BV_2177	BVn177								0
CM	GV2165	314		0	M2 Cooling Water Inlet Bypass Hand Valve	M2	MX	166	PCM2	156	R022	160	MPF	164		mGV	37	A170810-PR-SMS-PID-002		GV	2165	GV_2165	GVn165								0
CM	LC2101	315		0	M2 Load Cell	M2	MX	166	PCM2	156	R022	160	MPF	164		mLC1	52	A170810-PR-SMS-PID-002		LC	2101	LC_2101	LCn101								0
CM	LC2103	316		0	M2 Load Cell	M2	MX	166	PCM2	156	R022	160	MPF	164		mLC1	52	A170810-PR-SMS-PID-002		LC	2103	LC_2103	LCn103								0
CM	LC2102	317		0	M2 Load Cell	M2	MX	166	PCM2	156	R022	160	MPF	164		mLC1	52	A170810-PR-SMS-PID-002		LC	2102	LC_2102	LCn102								0
CM	PG2101	318		0	M2 Vent Filter Outlet Pressure	M2	MX	166	PCM2	156	R022	160	MPF	164		mPG	16	A170810-PR-SMS-PID-002		PG	2101	PG_2101	PGn101								0
CM	PG4101	319		0	S2 Vent Filter Outlet Pressure	S2	SY	172	PCS2	158	R024	161	MPF	164		mPG	16	A170810-PR-SMS-PID-003		PG	4101	PG_4101	PGn101								0
CM	ST2101	320		0	M2 CA Supply Line Drain Steam Trap	M2	MX	166	PCM2	156	R022	160	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	2101	ST_2101	STn101								0
CM	ST2103	321		0	M2 Vent Filter Drain Line Steam Trap	M2	MX	166	PCM2	156	R022	160	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	2103	ST_2103	STn103								0
CM	ST2105	322		0	M2 Outline Line Steam Trap	M2	MX	166	PCM2	156	R022	160	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	2105	ST_2105	STn105								0
CM	ST2107	323		0	SMFL2 Filtration Line Steam Trap	M2	MX	166	PCM2	156	R022	160	MPF	164		mST	25	A170810-PR-SMS-PID-002		ST	2107	ST_2107	STn107								0
CM	ST4101	324		0	S2 CA Supply Line Drain Steam Trap	S2	SY	172	PCS2	158	R024	161	MPF	164		mST	25	A170810-PR-SMS-PID-003		ST	4101	ST_4101	STn101								0
CM	ST4103	325		0	S2 Vent filter drain line steam trap	S2	SY	172	PCS2	158	R024	161	MPF	164		mST	25	A170810-PR-SMS-PID-003		ST	4103	ST_4103	STn103								0
CM	ST4105	326		0	S2 Outlet Line steam trap	S2	SY	172	PCS2	158	R024	161	MPF	164		mST	25	A170810-PR-SMS-PID-003		ST	4105	ST_4105	STn105								0
CM	XLC2101	327		0	M2 Vessel Light	M2	MX	166	PCM2	156	R022	160	MPF	164		mSG	23	A170810-PR-SMS-PID-002		XLC	2101	XLC_2101	XLCn101								0
CM	XLC4101	328		0	S2 Vessel Light	S2	SY	172	PCS2	158	R024	161	MPF	164		mSG	23	A170810-PR-SMS-PID-003		XLC	4101	XLC_4101	XLCn101								0
CM	XW2117	329		0	M2 Spray Ball 1	M2	MX	166	PCM2	156	R022	160	MPF	164		mSB	22	A170810-PR-SMS-PID-002		XW	2117	XW_2117	XWn117								0
CM	XW2119	330		0	M2 Spray Ball 2	M2	MX	166	PCM2	156	R022	160	MPF	164		mSB	22	A170810-PR-SMS-PID-002		XW	2119	XW_2119	XWn119								0
CM	XW4117	331		0	S2 Spray Ball 1	S2	SY	172	PCS2	158	R024	161	MPF	164		mSB	22	A170810-PR-SMS-PID-003		XW	4117	XW_4117	XWn117								0
CM	XW4119	332		0	S2 Spray Ball 2	S2	SY	172	PCS2	158	R024	161	MPF	164		mSB	22	A170810-PR-SMS-PID-003		XW	4119	XW_4119	XWn119								0
CM	ZSC4111	333	ZSC2	27	VTL2 to M1 Flowpath Indicator	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3111	ZSC_3111	ZSCn111	ZSC2	ZSC_SMFL1	_zsc_smfl1					0
CM	ZSC4113	334	ZSC2	27	VTL2 to M2 Flowpath Indicator	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3113	ZSC_3113	ZSCn113	ZSC2	ZSC_FILTER	_zsc_filter					0
CM	DV4123	335	POS2	21	S2 Transfer line valve from vessel	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mDV3	8	A170810-PR-SMS-PID-003		DV	3123	DV_3123	DVn123	POS2	POS_VESSEL	_pos_vessel					0
CM	DV4125	336	POS2	21	S2 Transfer line valve from SMFL	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mDV3	8	A170810-PR-SMS-PID-003		DV	3125	DV_3125	DVn125	POS2	POS_SMFL	_pos_smfl					0
CM	DV4127	337	POS2	21	S2 Transfer line valve to drain	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mDV3	8	A170810-PR-SMS-PID-003		DV	3127	DV_3127	DVn127	POS2	POS_DRAIN	_pos_drain					0
CM	DV4129	338	POS2	21	S2 Transfer line valve to filling	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mDV3	8	A170810-PR-SMS-PID-003		DV	3129	DV_3129	DVn129	POS2	POS_FILL	_pos_fill					0
CM	ZSC4115	339	ZSC2	27	S2 to F1P1 Flowpath Indicator	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3115	ZSC_3115	ZSCn115	ZSC2	ZSC_CIPSIP	_zsc_cipsip					0
CM	ZSC4117	340	ZSC2	27	S2 to F2P1 Flowpath Indicator	EX4007	EMX2	306	S2	172	PCS2	158	R024	161	306	mPROX1	18	A170810-PR-SMS-PID-003		ZSC	3117	ZSC_3117	ZSCn117	ZSC2	ZSC_BFS2	_zsc_bfs2					0

## tblClass
Level	Class	ID	Description	Interlock	sfcMarker	ifb	ifc	fb	Hygiene	Timer
IO	DI	1	Digital Input	#INTERLOCK;		DEL	DEL	DEL
IO	DO	2	Digital Output	#INTERLOCK;		DEL	DEL	DEL
IO	AI	3	Analog Input	#INTERLOCK;		DEL	DEL	DEL
IO	AO	4	Analog Output	#INTERLOCK;		DEL	DEL	DEL
IO	PDI	5	Profinet Digital Input	#INTERLOCK;		DEL	DEL	DEL
IO	PDO	6	Profinet Digital Output	#INTERLOCK;		DEL	DEL	DEL
IO	PAI	7	Profinet Analog Input	#INTERLOCK;		DEL	DEL	DEL
IO	PAO	8	Profinet Analog Output	#INTERLOCK;		DEL	DEL	DEL
IL	IL1	9	Interlock Calculation with 1 input	#INTERLOCK;		ifbIL1	ifcIL1	fbIL1
IL	IL2	10	Interlock Calculation with 2 inputs	#INTERLOCK;		ifbIL2	ifcIL2	fbIL2
IL	IL3	11	Interlock Calculation with 3 inputs	#INTERLOCK;		ifbIL3	ifcIL3	fbIL3
IL	IL4	12	Interlock Calculation with 4 inputs	#INTERLOCK;		ifbIL4	ifcIL4	fbIL4
IL	IL5	13	Interlock Calculation with 5 inputs	#INTERLOCK;		ifbIL5	ifcIL5	fbIL5
IL	IL6	14	Interlock Calculation with 6 inputs	#INTERLOCK;		ifbIL6	ifcIL6	fbIL6
CM	DI1	15	General alarm single digital input	"idbDI1".@@INSTANCE@@.DI_PV;	_di_	ifbDI1	ifcDI1	fbDI1
CM	DI2	16	General alarm software module without field input	"idbDI2".@@INSTANCE@@.DI_PV;	_di_	ifbDI2	ifcDI2	fbDI2
CM	HE1	17	Vessel vent filter Electric Heating Element	#INTERLOCK;	_he_	ifbHE1	ifcHE1	fbHE1
CM	MI1	18	Load cell mass indicator	#INTERLOCK;	_mi_	ifbMI1	ifcMI1	fbMI1
CM	MOD1	19	Modulating control valve	#INTERLOCK;	_mod_	ifbMOD1	ifcMOD1	fbMOD1
CM	MOT1	20	Vacuum pump motor	#INTERLOCK;	_mot_	ifbMOT1	ifcMOT1	fbMOT1
CM	PI1	21	Vessel Pressure Indictor	#INTERLOCK;	_pi_	ifbPI1	ifcPI1	fbPI1
CM	PC1	22	Vessel ON/OFF pressure control loop with output valve selection	#INTERLOCK;	_pc_	ifbPC1	ifcPC1	fbPC1
CM	POS1	23	On/Off valve with single output and no feedback	(; / L "idbPOS1".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	_pos_	ifbPOS1	ifcPOSx	fbPOSx
CM	POS2	24	On/Off valve with single output and closed position feedback	(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	_pos_	ifbPOS2	ifcPOSx	fbPOSx
CM	POS3	25	On/Off valve with single output and opened position feedback	(; / L "idbPOS3".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	_pos_	ifbPOS3	ifcPOSx	fbPOSx
CM	POS4	26	On/Off valve with single output and both opened and closed feedback	(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	_pos_	ifbPOS4	ifcPOSx	fbPOSx
CM	SIC1	27	Agitator speed control	#INTERLOCK;	_sic_	ifbSIC1	ifcSIC1	fbSIC1
CM	TC1	28	Heat exchanger cooling only temperature controller	#INTERLOCK;	_tc_	ifbTC1	ifcTC1	fbTC1
CM	TI1	29	Vessel temperature Indicator with alarms and interlocks	#INTERLOCK;	_ti_	ifbTI1	ifcTI1	fbTI1
CM	TI2	30	Line mounted temperature indicator	#INTERLOCK;	_ti_	ifbTI2	ifcTI2	fbTI2
CM	ZSC1	31	Manway closed indication and alarm	"idbZSC1".@@INSTANCE@@.DI_PV;	_zsc_	ifbZSC1	ifcZSC1	fbZSC1
CM	ZSC2	32	Flow path connection indication	"idbZSC2".@@INSTANCE@@.DI_PV;	_zsc_	ifbZSC2	ifcZSC2	fbZSC2
EM	EMA1	33	Manufacturing vessel agitator	#INTERLOCK;	_ema1_	ifbBLK	ifcBLK	fbBLK		Yes
EM	EMC1	34	Vessel LP CA and HP CA supply, Vacuum and Vent	#INTERLOCK;	_emc1_	ifbBLK	ifcBLK	fbBLK
EM	EMC2	35	WFI, PS(WFI) supply and PW, PS(PW) supply to manufacturing vessel	#INTERLOCK;	_emc_	ifbBLK	ifcBLK	fbBLK		Yes
EM	EMC3	36	WFI, PS(WFI) supply and PW, PS(PW) supply to storage vessel	#INTERLOCK;	_emc_	ifbBLK	ifcBLK	fbBLK		Yes
EM	EMC5	37	Vacuum system	#INTERLOCK;	_emc_	ifbBLK	ifcBLK	fbBLK		Yes
EM	EMG1	38	Vessel gas filter heating element and temperature indicator, drain valve and filter outlet line temperature indicator	#INTERLOCK;	_emg_	ifbBLK	ifcBLK	fbBLK
EM	EMM1	39	Manufacturing vessel load cell	#INTERLOCK;	_emm_	ifbBLK	ifcBLK	fbBLK
EM	EMS1	40	ESTOP	#INTERLOCK;	_ems_	ifbBLK	ifcBLK	fbBLK
EM	EMT1	41	Manufacturing filtration line heat exchanger cooling control	#INTERLOCK;	_emt_	ifbBLK	ifcBLK	fbBLK
EM	EMV1	42	Vessels manway, bursting disc, bottom outlet valve and temperature alarms and interlocks	#INTERLOCK;	_emv_	ifbBLK	ifcBLK	fbBLK
EM	EMV2	43	Vessel Inlet Sprayball Valves	#INTERLOCK;	_emv_	ifbBLK	ifcBLK	fbBLK		Yes
EM	EMX1	44	Manufacturing vessel filtration line MMFLx	#INTERLOCK;	_emx_	ifbBLK	ifcBLK	fbBLK
EM	EMX2	45	Vessels Transfer Lines	#INTERLOCK;	_emx_	ifbBLK	ifcBLK	fbBLK
EM	EMX4	46	CIP & SIP Drain	#INTERLOCK;	_emx_	ifbBLK	ifcBLK	fbBLK
EM	EMX5	47	BFS Inlet Filling Line	#INTERLOCK;	_emx_	ifbBLK	ifcBLK	fbBLK
EM	EMX6	48	Filtration line SMFLx to Vessels Transfer Lines	#INTERLOCK;	_emx_	ifbBLK	ifcBLK	fbBLK
PC	PCSMS	49	Solution Manufacturing System Process Cell	#INTERLOCK;	_pcsms_	ifbBLK	ifcBLK	fbBLK
PC	PCSTOR	50	Storage Vessels Process Cell	#INTERLOCK;	_pcstor_	ifbBLK	ifcBLK	fbBLK
RM	ROOM	51	Room	#INTERLOCK;		ifbBLK	ifcBLK	fbBLK
UN	FLZ	52	Filling Line	#INTERLOCK;	_fpz_	ifbBLK	ifcBLK	fbBLK	Yes
UN	MX	53	Manufacturing Vessel and associated equipment	#INTERLOCK;	_mx_	ifbBLK	ifcBLK	fbBLK	Yes
UN	SMFL	54	Manufacturing Vessel Filtration Outlet Line to Storage and Filling	#INTERLOCK;	_smflx_	ifbBLK	ifcBLK	fbBLK	Yes
UN	SY	55	Storage Vessel and associated equipment	#INTERLOCK;	_sy_	ifbBLK	ifcBLK	fbBLK	Yes
UN	VTL	56	Vessel Transfer Lines	#INTERLOCK;	_vtl_	ifbBLK	ifcBLK	fbBLK	Yes
SI	SITE	57	MPF Site	#INTERLOCK;
SH	SHARE	58	Shared object which can be acquired (has no parent)	#INTERLOCK;

## tblClass_Physical
Class	ID	Description	Make	Model	LINK TO DATASHEET	EM Class	Gasket	MaterialSpec	Material	Service Requirements	Functional Requirements	Control Requirements	Material Requirements	Size	Installation Requirements	Surface Finish Required	Seals Required	Material Certification Required	Surface Finish Certification Required	Supplier	Wetted Components	Surface Finish	Seals	Recommended Spares	Remarks	Pneumatic Hose Size	fatSy	fatMx
mAGT	1	Vessel Mixer Agitator	Millipore	Merck Novaseptic GMP20000 Agitator set (inclusive with gearbox, motor & corresponding inverter)	Proposed by Vessel Manufacturer	EMA1	N/A	AISI	Stainless Steel 316L	Motor: 0.75 4P kW 440V 50Hz, suitable for running with inverter	N/A	VFD to have profinet connectibility	Stainless Steel 316L	N/A	Magnetic Impeller	Ra <0.5 um	N/A	1	1	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	N/A		N/A		Y
mASL	2	Pressure Switch	Festo	PEV-1/4-SC-OD	https://www.festo.com/net/SupportPortal/Files/320479/PEV-14-B-SC_2003-02c_386354d3.pdf	N/A	N/A	N/A	Aluminium (coated)	N/A	1 - 12 bar. IP65	N/A	N/A	N/A	G 1/4 pnuematic connection	N/A	N/A	N/A	N/A	CCT Automation	N/A	N/A	N/A	N/A		6 mm
mCOUP	3	Hansen Couplings	Eaton	1. Female Socket: ML12H46-BS 1.1/2'' modify to ferrule end (Qty: 4) / 2. Male Plug: ML12H46-BS 1.1/2'' modify to ferrule end (Qty: 12)	http://www.vpcsolucionesindustriales.com.co/images/CatalogoEATON.pdf	N/A	EPDM	AISI	Stainless Steel 316L	6 bar	N/A	N/A	Stainless Steel 316L	2"	Machine to remove BSP thread	N/A	N/A	1	0	JJK Engineering	N/A	N/A	N/A	N/A		N/A
mCV	4	Pneumatic Control Valve	Samson	Valve: Type 3241-1 / Actuator: Type 3271	Valve: / https://www.samson.de/document/t80120en.pdf / Actuator: https://www.samson.de/document/e83106en.pdf	EMT1	NBR	AISI	Stainless Steel 316L	Press. 3 bar / Temp -10 to 220 degC	Normally Closed	Pneumanitically Actuated Control Valve	N/A	DN 80	Flange	N/A	NBR	0	0	Dancomech Engineering	N/A	N/A	N/A	Diaphragm Seals		6 mm
mDV	5	Shutoff valve for 1 inch pipe, triclamp, normally-open stainless steel actuator	Millipore	Valve: NU100/311-212 / Actuator: PA25/100 / Diaphragm: NA25/22 / Position Indicator: PA1251/SP	http://www.merckmillipore.com/SG/en/Products/8VKb.qB.qhAAAAFBLR8e15j1,nav	EMC1	EPDM	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Open	Pneumanitically Actuated Valve with Closed feed back	Stainless Steel 316L	1"	Tri-clamp	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	Diaphragm Seals	Shut off 180 valve for 1in (normal Open)	6 mm
mDV1	6	Shutoff valve for 1 inch pipe, triclamp, normally-closed plastic actuator	Millipore	Valve: NU100/311-212 / Actuator: PA25/111 / Diaphragm: NA25/22 / Position Indicator: PA1251/SP	http://www.merckmillipore.com/SG/en/Products/8VKb.qB.qhAAAAFBLR8e15j1,nav	EMC1 / EMV2	EPDM	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with closed feed back	Stainless Steel 316L	1"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	Diaphragm Seals	Shut off 180 valve for 1in	6 mm
mDV2	7	Shutoff valve for 1.5 inch pipe, triclamp, normally-closed plastic actuator	Millipore	Valve: NU150/311-212 / Actuator: PA38/111 / Diaphragm: NA38/22 / Position Indicator: PA1251/SP	http://www.merckmillipore.com/SG/en/Products/8VKb.qB.qhAAAAFBLR8e15j1,nav	EMX6	EPDM	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Closed feed back	Stainless Steel 316L	1.5"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	Diaphragm Seals	Shut off 180 valve for 1½in	6 mm
mDV3	8	Shutoff valve for 2 inch pipe, triclamp, normally-closed plastic actuator (EPDM seat)	Millipore	Valve: NU200/311-212 / Actuator: PA51/111 / Diaphragm: NA51/22 / Position Indicator: PA1251/SP	http://www.merckmillipore.com/SG/en/Products/8VKb.qB.qhAAAAFBLR8e15j1,nav	EMC1 / EMX1 / EMX2	EPDM	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Closed feed back	Stainless Steel 316L	2"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	Diaphragm Seals	Divert valve for 2in	6 mm
mDV4	9	Tank outlet valve for 2 inch, buttweld, normally-closed plastic actuator	Millipore	Valve: NU200/442-312 / Actuator: PA51/111 / Diaphragm: NA51/22 / Position Indicator: PA1251/SP	http://www.merckmillipore.com/SG/en/Products/8VKb.qB.qhAAAAFBLR8e15j1,nav	EMV1	EPDM	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Closed feed back	Stainless Steel 316L	2"	Buttweld	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	Diaphragm Seals	Position indicator for NA51, w. output signal	6 mm	Y	Y
mDV5	10	Provided by Rieckermann Thailand (Actuated Valve)				EMC2 / EMC3					N/A															N/A
mDV6	11	Shutoff valve for 2 inch pipe, triclamp, normally-closed plastic actuator (PTFE seat)	Millipore	Valve: NU200/311-212 / Actuator: PA51/111 / Diaphragm: NA51/25 / Position Indicator: PA1251/SP	http://www.merckmillipore.com/SG/en/Products/8VKb.qB.qhAAAAFBLR8e15j1,nav	EMC2 / EMC3	PTFE	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Closed feed back	Stainless Steel 316L	2"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	N/A	Divert valve for 2in	6 mm
mFILT	12	Vent Filter Housing / Vent Filter Element	Millipore	Housing: H1UE7T1G01PC / Filter Element: CTGB71TP3	S:\Projects\Projects17\A170810 - MPI SMS\05. Detailed Design\04. Working Documents\MPI.SMS\Quotations & PO\Data Sheets	EMG1	PTFE/EPDM/USP Class 6/FDA approved material	ASME	Housing: Stainless Steel 316L / Filter Element: PTFE	10 Barg @140 deg C (Maximum)	trace heater: 240 V (50 hz)/ AB05/AB02 code 2 cartridge	N/A	Stainless Steel 316L	Inlet/Outlet: 1" Vent: 1/2" & Drain: 1/2" / Heater: TBA (supplier to match with selected Vent filter)	Ferrule (Tri-Clamp)	Housing Wetted Surface: Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Housing: Ra ≤ 0.5 uM	Silicone O ring/EPDM/PTFE	O-ring / Filter Element		N/A
mHE	13	Vent Filter Heating Element	Millipore	HJ230-104/270	Specification\HJ230-104270 Drawing (Heating Jacket).pdf	EMG1	N/A	N/A	NA	Operating Material: 230 VAC +/-10%, / Power Consumption: max. 70 W	IP Rating: IP 54	N/A	N/A	N/A	N/A	N/A	N/A	N/A	N/A	Merck	N/A	N/A	N/A	N/A		N/A
mHMI	14	TP1900 Comfort INOX Touch Screen HMI	Siemens	6AV2144-8UC10-0AA0	https://mall.industry.siemens.com/mall/en/WW/Catalog/Product/6AV2144-8UC10-0AA0		N/A	N/A	Stainless Steel 316L (Enclosure)	N/A	SIMATIC HMI TP1900 COMFORT INOX STAINLESS STEEL / FRONT, MEMBRANE COVERING DISPLAY, PROTECTION CLASS / FRONT IP66K, 19" WIDESCREEN-TFT-DISPLAY, PROFINET / INTERFACE, MPI/PROFIBUS DP INTERFACE, 24 MB USER / MEMORY, WINDOWS CE 6.0, CONFIGURABLE FROM WINCC / COMFORT V11 SP2	24 VDC, 32 W, X86 processor, 2 port industrial ethernet interfaces, 2 usb port (usb 2.0)/1 usb mini B (5 pole), profinet/profinet IO/EtherNetIP/IRT/MRP/profibus/MPI/TCPIP/DHCP/SNMP/DCP/LLDP (protocols), HTTP/HTTPS/HTML/XML/CSS/JavaScript (WEB characteristics), upt 128 MB MMC and up to 2 GB SD card	INOX stainless steel front		N/A	N/A	N/A	0	0		N/A	N/A	N/A	N/A		N/A
mPC	15	Batch PC	HP	dc7900 Convertible Minitower	http://www.hp.com/ctg/Manual/c01549447.pdf		N/A	N/A	N/A	HP L1710 17-inch LCD Monitor SING	Intel Core 2 Duo E8400 Processor (3.0 GHz, 6 MB L2 cache, 1333 MHz FSB), 4GB PC2-6400 (DDR2-800) 2x2GB, 320GB SATA 3.5 1st Hard Drive	N/A	N/A	N/A	N/A	N/A	N/A	0	0		N/A	N/A	N/A	N/A		N/A
mPG	16	Pressure gauge	Milipore	P90005	http://www.merckmillipore.com/MY/en/search/P90005?search=&TrackingSearchType=SB+-+Search+Box&SearchContextPageletUUID=&SearchTerm=P90005	MX / SY	N/A	AISI	Stainless Steel 316L	0 - 1,100 Kpa	N/A	N/A	N/A	to match selected vent filter housing	Ferrule (Tri-Clamp)	N/A	Diaphragm Seal	1	0	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A
mPROX	17	Proximity sensor	ifm electronic gmbh	IGT200	IGT200-00_EN-GB.pdf	EMV1	N/A	N/A	N/A	10….36 VDC	Normally Open	3 Wire DC PNP	N/A	M12x1 or M18x1	IP68; IP 69K; M18 connector	N/A	N/A	0	0	ifm electronic Pte Ltd	N/A	N/A	N/A	N/A		N/A
mPROX1	18	Proximity sensor	ifm electronic gmbh	IFT200	https://www.ifm.com/gb/en/product/IFT200	EMC2 / EMC3 / EMX1 / EMX2 / EMX6	N/A	N/A	N/A	10….36 VDC	Normally Open	3 Wire DC PNP	N/A	M12x1	IP68; IP 69K; M12 connector	N/A	N/A	0	0	ifm electronic Pte Ltd	N/A	N/A	N/A	N/A		N/A
mPRT	19	Batch Report Printer	HP	HP Color LaserJet CP3525dn	http://www.printerworks.com/DataSheets/CP3525datasheet.pdf		N/A	N/A	N/A	HP 3 Years Next Business Day Onsite CP3525 series HW Supp	Print: Up to 30 ppm black & Up to 30 ppm colour; Up to 600 x 600 dpi; Up to / 75,000 pages duty cycle; 384 MB; 1 embedded HP Jetdirect 10/100/1000 Base-T / Ethernet, 1 USB-B Plug and Play; 515 MHz processor speed; Duplex	N/A	N/A	N/A	N/A	N/A	N/A	0	0		N/A	N/A	N/A	N/A		N/A
mPT	20	Pressure Indicating Transmitter	Endress+Hauser	PMP55-4JXF0/0	https://portal.endress.com/wa001/sap(bD1lbiZjPTIwMA==)/bc/bsp/euh/dla/extern/detail.htm?no_heading=x&xmaster=x&xdesign=x&language=en&key=DLA000000000000005000498675301000	EMC1	Membrane AISI 316	AISI	N/A	10 bar - 40 bar	With Local Display	4 - 20 mA output/supply voltage 11.5 - 45 VDC	N/A	1-1/2"	Ferrule (Tri-Clamp)	N/A	Diaphragm Seal	1	0	Endress+Hauser	SS 316L/1.4435	Ra < 0.38 um	N/A	N/A		N/A
mRD	21	Bursting disc	Fike	Axius SC	S:\Projects\Projects17\A170810 - MPI SMS\05. Detailed Design\04. Working Documents\MPI.SMS\Quotations & PO\Data Sheets	EMV1	Silicone Platinum Cured	ASME	Stainless Steel 316L	Mixing Vessel: 4 bar @ 150 deg C / Storage Vessel: 3 bar @ 150 deg C	Full vacuum	With burst indicator	N/A	1 1/2" (DN40)	Ferrule (Tri-Clamp)	Ra 12-25 um	Silicone Platinum Cured	1	1	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	Bursting Discs		N/A
mSB	22	Spray ball	Aerre Inox	TR-C-weld end	S:\Projects\Projects17\A170810 - MPI SMS\05. Detailed Design\04. Working Documents\MPI.SMS\Quotations & PO\Data Sheets	MX / SY	N/A	AISI	Stainless Steel 316L	4,100 - 6,300 liter per hour at 1 - 3 bar	360 degree spray pattern	N/A	N/A	3/4"	Ferrule (Tri-Clamp) on Vessel	Ra < 0.5 um		1	1	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A	Y	Y
mSG	23	Sight Glass Vessel Luminare - w Light fitting	Max Muller AG	BKVLR 100HD	miniLUX BKVLR.pdf	MX / SY	Corrosion & Alteration resistant	AISI	Stainless Steel 316L / / GLASS	24 VDC/VAC 100 Watt	N/A	N/A	N/A	to match selected sight glass	IP65	N/A	N/A	0	0	JJK Engineering	SS 316L/1.4435 & Glass	Ra ≤ 0.5 uM	N/A	N/A		N/A	Y	Y
mSOL	24	SMS1 remote solenoid valve and digital input station	Festo	MPA-FB-VI	https://www.festo.com/net/et_ee/SupportPortal/default.aspx?q=530411		N/A	N/A	N/A	6 bar Dried compressed air of quality class 5 to DIN ISO 8573-1 lubricated or unlubricated, Max operating pressure 10 bar and maximum control pressure 8 bar	24 VDC +/- 25%, 8A power supply per supply contact, 2.5 A max current loading of the valve voltage, max switching frequency 10 Hz, 50% Max pulse ratio at 10 Hz, safety class 3, IP 54	Profinet	All aluminium alloys used contain less than 7.5 % magnesium (Mg) by mass housing	N/A	In cabinet, complete with all required components for the purpose	N/A	Elastomer, NBR seals	0	0	CCT Automation	N/A	N/A	N/A			N/A
mST	25	Steam trap	Spirax Sarco	BT6-B	http://www.spiraxsarco.com/global/us/Products/Documents/BT6-B_Sanitary_Balanced_Pressure_Thermostatic_Steam_Trap-Technical_Information.pdf	MX / SY	N/A	AISI	Stainless Steel 316L	N/A	N/A	N/A	Stainless Steel 316L	1/2" & 1 1/2"	Ferrule (Tri-Clamp)	Ra ≤ 0.6 uM	N/A	1	1	Spirax Sarco	SS 316L/1.4435	Ra ≤ 0.6 uM	EPDM/PTFE	N/A		N/A
mT	26	Temperature probe c/w transmitter (with 35 mm neck)	Endress+Hauser	TMR35-A1BBDBAC2CBA	TI00123REN_1416.pdf	EMX4	N/A	N/A	N/A	0 - 150 deg C	Pt 100 sensing element with class A / accuracy (DIN EN 60751)	4 - 20 mA output signal	N/A	1-1/2"	Tri-Clamp (line mounted; tundish/drain)	N/A	Diaphragm EPDM/PTFE	1	1	Endress+Hauser	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A
mTT	27	Temperature Transmitter of Heating Jacket	Milipore	Type 2 Wire PT100 (Milipore)	Specification\HJ230-104270 Drawing (Heating Jacket).pdf		N/A	N/A	N/A	PT100 3W 0 - 150 deg C	N/A	PT100	N/A	To match Filter Housing	N/A	N/A	N/A	0	0	Merck	N/A	N/A	N/A	N/A		N/A
mTT1	28	Temperature Transmitter with Hygienic Thermowell	Endress+Hauser	TM411	http://endress.org.ua/pdf/MTR44.pdf	EMT1	N/A	N/A	N/A	0 - 150 deg C	Pt 100 sensing element with class A / accuracy (DIN EN 60751)	4 - 20 mA output signal	Stainless Steel 316L	1-1/2"	Tri-Clamp (line mounted; product contact)	N/A	N/A	0	0	Endress+Hauser	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A
mUPS	29	Un-interruptible Power Supply	APC by Schneider Electric	APC Back-UPS CS 500VA, 230V	CLII-9BLHVF_R0_EN.pdf		N/A	N/A	N/A	N/A	Protects connected loads from surges, spikes, lightning, and other power disturbances. Reserves power capacity and run time for connected equipment that require battery back-up while providing surge only protection for less critical equipment.	Interface Port DB-9 RS-232, USB	N/A	N/A	N/A	N/A	N/A	0	0		N/A	N/A	N/A	N/A		N/A
mVP	30	Vacuum pump	Elmo Rietschle	VC 202	http://vactech.com.my/wp-content/uploads/2014/02/VC-202-VC-303.pdf	EMC5	N/A	N/A	N/A	Oil Rotary Vane	Capacity: 200 m³ / hour / Vacuum: 0.1 mbar (abs.) /-0.99 bar	N/A	N/A	2"	Threaded 2" BSP	N/A	N/A	0	0	Vactech Sdn. Bhd	N/A	N/A	N/A	N/A		N/A
mBAV1	31	Ball Valve 1/2" (actuated)	Meca INOX	Valve Model: PS4LBWNI / Actuator Model: PA00S(4+4)	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	EMC1 / EMG1	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Open & Closed feed back	Valve Body: SS 316L / Ball: SS316L	1/2"	Buttweld	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	TFM 1600	N/A		8mm
mBAV2	32	Ball Valve 1" (manual)	Meca INOX	PS4LBWNI	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	MX / SY	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	N/A	Manually Operated with no feed back	Valve Body: SS 316L / Ball: SS316L	1"	Buttweld	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	TFM 1600	N/A		N/A
mBAV3	33	Ball Valve 3/4" (actuated)	Meca INOX	Valve Model: PS4LBWNA / Actuator Model: PA05S(5+5)	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	EMT1	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 5 bar, Temp 30 degC	Normally Closed	Pneumanitically Actuated Valve with Open & Closed feed back	Valve Body: Carbon Steel / Ball: SS316L	3/4"	Buttweld	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	Carbon Steel: ASTM A216 WCB / ASTM A351 CF3M	N/A	TFM 1600	N/A		8mm
mBAV4	34	Ball Valve 1-1/2" (actuated)	Meca INOX	Valve Model: PS4LBWNI / Actuator Model: PA10S(4+4)	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	EMX4	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 5 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Open & Closed feed back	Valve Body: SS 316L / Ball: SS316L	1-1/2"	Buttweld	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	TFM 1600	N/A		8mm
mBAV5	35	Ball Valve 2" (actuated)	Meca INOX	Valve Model: PS4LBWNI / Actuator Model: PA20S(5+5)	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	EMX4	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 5 bar, Temp 160 degC	Normally Closed	Pneumanitically Actuated Valve with Open & Closed feed back	Valve Body: SS 316L / Ball: SS316L	2"	Buttweld	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	TFM 1600	N/A		8mm
mBV6	36	Butterfly Valve 4" (manual)	KSB AMRI	KABOAXBS4LN-100	http://www.dancomech.com.my/product/456/KSB-AMRI---Butterfly-Valve-(Concentric-Type)/	MX	EPDM	ASTM	Cast Iron	Press. 5 bar, Temp 30 degC	N/A	Manually Operated with no feed back	Cast Iron	4"	Flange	N/A	NBR	0	0	Dancomech Engineering	Cast Iron	N/A	EPDM	N/A		N/A
mGV	37	Gate Valve 4" (manual)	VMXZ4 (Dancomech)	VMXZ4-5141P16F1-080	http://www.dancomech.com.my/product/604/VMX---Gate-Valve/	MX	Graphite	AISI	Cast Iron	Press. 5 bar, Temp 30 degC	N/A	Manually Operated with no feed back	Cast Iron	3"	Flange	N/A	Brass with Cromium	0	0	Dancomech Engineering	Cast Iron	N/A	Graphite	N/A		N/A
mESTOP	38	Emergency Stop	IDEC	HW1B-X401R	http://eu.idec.com/en/download/download.aspx?download=EP14301EstopHW2	EMS1	N/A	N/A	N/A	1 NC Signal when activated	Normally Closed	Press button to activate EStop. The button is released by turning the key clockwise	N/A	N/A	N/A	N/A	N/A	0	0	Macro Integration	N/A	N/A	N/A	N/A	Key Released	N/A
mESTOP1	39	Emergency Stop	IDEC	HW1B-X402R	http://eu.idec.com/en/download/download.aspx?download=EP14301EstopHW2	EMS1	N/A	N/A	N/A	2 NC Signal when activated	Normally Closed	Press button to activate EStop. The button is released by turning the key clockwise	N/A	N/A	N/A	N/A	N/A	0	0	Macro Integration	N/A	N/A	N/A	N/A	Key Released	N/A
mBV7	40	Butterfly Valve 4" (actuated)	KSB AMRI	Valve: KABOAXBS4LN-100 / Actuator: FSAS0053-F0507V17 / Position Indicator: LSB-10007E2N2	http://www.dancomech.com.my/product/456/KSB-AMRI---Butterfly-Valve-(Concentric-Type)/	EMT1	EPDM	ASTM	Cast Iron	Press. 5 bar, Temp 60 degC	N/A	Pneumanitically Actuated Valve with Open & Closed feed back	Cast Iron	4"	Flange	N/A	NBR	0	0	Dancomech Engineering	Cast Iron	N/A	EPDM/PTFE	N/A		6 mm
mBAV6	41	Ball Valve 1/2" (manual)	Meca INOX	PS4LBWNI	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	MX	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	N/A	Manually Operated with no feed back	Valve Body: SS 316L / Ball: SS316L	1/2"	Orbital Welded	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	TFM 1600	N/A	Orbital Welded	N/A
mPB	42	Push Button	Schneider	XB5 Illuminated White Push Button NO/NC Spring Return	https://uk.rs-online.com/web/p/push-button-complete-units/6096338/?origin=PSF_421270|alt		N/A	N/A	N/A	Integral LED/IP67/circular head	1NO + 1NC	24 V AC/DC	N/A	N/A	Panel Mount	N/A	N/A	0	0		N/A	N/A	N/A	N/A		N/A
mT1	43	Temperature probe c/w transmitter (with 35 mm neck)	Endress+Hauser	TMR35-A1BBDLAC2CBA	TI00123REN_1416.pdf	EMX4	N/A	N/A	Stainless Steel 316L	0 - 150 deg C	Pt 100 sensing element with class A / accuracy (DIN EN 60751)	4 - 20 mA output signal	N/A	2"	Tri-Clamp (line mounted; tundish/drain)	N/A	Diaphragm EPDM/PTFE	0	0	Endress+Hauser	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A
mT2	44	Temperature probe c/w transmitter (with 35 mm neck)	Endress+Hauser	TMR35-A1BBDMC2CBA	TI00123REN_1416.pdf	EMG1	N/A	N/A	Stainless Steel 316L	0 - 150 deg C	Pt 100 sensing element with class A / accuracy (DIN EN 60751)	4 - 20 mA output signal	N/A	1"	Tri-Clamp (line mounted; vent filter)	N/A	Diaphragm EPDM/PTFE	0	0	Endress+Hauser	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A
mPRV	45	Pressure Regulating Valve	Parker	P3NRA98BNN	https://www.parker.com/literature/Literature%20Files/pneumatic/Literature/PDN1000US_Products/PDN1000-3_Products/PDN1000-3US_P3NR.pdf	MX / SY	N/A	N/A	Aluminium	Operating Range: / Inlet: 6 to 7 bar / Oulet: 2 to 3 bar	N/A	Manually Operated with no feed back	N/A	1"	Fabricate both end with 1 inch SS316 ferrule adaptor	N/A	N/A	0	0	JJK Engineering	Aluminum	N/A	Nitrile	N/A		N/A
mFILT1	46	Compressed Air Filter	Milipore	Filter: CTGB71TP3 (Aerex) / Housing: H1AV7TG01PP	Filter: http://www.merckmillipore.com/MY/en/product/Aerex-CTGB-Cartridge-Filter-10nbspin.-0.2nbspm-Code-7,MM_NF-CTGB71TP3 / Housing: http://www.merckmillipore.com/MY/en/product/Series-3000-Single-Round-Housings,MM_NF-C100748	MX / SY	EPDM	N/A	Pre-Filter: Polypropylene / Housing: Stainless Steel 316L	10" Filter Element; 0.2 micron	Air Filter	N/A	N/A	50cm x 7cm dia	Ferrule (Tri-Clamp)	N/A	Silicone	0	0	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	Silicone O ring/EPDM/PTFE	O-ring / Filter Element		N/A
mFILT2	47	Filter Press	TBA by RT			MX				N/A	Liquid Filter	N/A	N/A	N/A	N/A											N/A
mFILT3	48	Pre-Filter Housing / Pre-Filter Element	Milipore	Pre-Filter: CR0172006 (Polygard) / Housing: H1AV7T2G01PP	Filter: http://www.merckmillipore.com/MY/en/product/Polygard-CR-Cartridge-Filter-20nbspin.-1.0nbspm-Code-7-Silicone,MM_NF-CR0172006 / Housing: http://www.merckmillipore.com/MY/en/product/Series-3000-Single-Round-Housings,MM_NF-C100748	SMFL	EPDM	N/A	Pre-Filter: Polypropylene / Housing: Stainless Steel 316L	20" Filter Element; 1.0 micron	Liquid Filter	N/A	Housing:Stainless Steel 316L	50cm x 7cm dia	Ferrule (Tri-Clamp)	N/A	Silicone	0	0	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	Silicone O ring/EPDM/PTFE	O-ring / Filter Element		N/A
mFILT4	49	Sterile Filter Housing / Sterile Filter Element	Milipore	Filter: CVGL72TP3 (Durapore) / Housing: H1AV7T2G01PP	Filter: http://www.merckmillipore.com/MY/en/products/biopharmaceutical-manufacturing/downstream-processing/sterile-filtration/sterile-liquid/durapore/.ymb.qB.PpQAAAFDBU94saSR,nav / Housing: http://www.merckmillipore.com/MY/en/product/Series-3000-Single-Round-Housings,MM_NF-C100748	SMFL	EPDM	N/A	Pre-Filter: Polypropylene / Housing: Stainless Steel 316L	20" Filter Element; 0.22 micron	Liquid Filter	N/A	Housing:Stainless Steel 316L	50cm x 7cm dia	Ferrule (Tri-Clamp)	N/A	Silicone	0	0	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	Silicone O ring/EPDM/PTFE	O-ring / Filter Element		N/A
mFILT5	50	Vacuum Pump Moisture Trap - not ordered yet				EMC5			N/A	To Prevent Moisture from System from entering Vacuum Pump	N/A	N/A	N/A	2"	Ferrule (Tri-Clamp)								N/A	N/A		N/A
mDV14	51	Provided by Rieckermann Thailand (Manual Valve)				MX			N/A	N/A	N/A	N/A	N/A	N/A		Ra ≤ 0.5 uM	N/A	1	1				N/A			N/A
mLC1	52	Load Cells	Mettler Toledo	Load Cell: SWC415 PM SS / Precision Junction Box: AJB540S / Analog Scale: AC350; 30076689	https://www.mt.com/my/en/home/products/Industrial_Weighing_Solutions/AutomPrecision/load-cell-and-weigh-module/compression/SWC515-pinmount.html	MX	N/A	N/A	Stainless Steel 316L	Mounted on side of vessel	7.5 tonnes	With feedback to terminal module	N/A	N/A	N/A	N/A	N/A	N/A	N/A	JJK Engineering	N/A	N/A	N/A	N/A		N/A
	53	M1 Control Panel	N/A	N/A			N/A	N/A	N/A	N/A	N/A	N/A	N/A	2000 x 1000 x 400	N/A	N/A	N/A	0	0	CCT Automation	N/A	N/A	N/A	N/A		N/A
	54	S1 Control Panel	N/A	N/A			N/A	N/A	N/A	N/A	N/A	N/A	N/A	1600 x 1000 x 400	N/A	N/A	N/A	0	0	CCT Automation	N/A	N/A	N/A	N/A		N/A
	55	BFS Control Panel	N/A	N/A			N/A	N/A	N/A	N/A	N/A	N/A	N/A	1600 x 1000 x 400	N/A	N/A	N/A	0	0	CCT Automation	N/A	N/A	N/A	N/A		N/A
mLAF	56	Laminar Flow Cabinet	Esco	Airstream Gen 3	http://www.escoglobal.com/product/laminar-flow-cabinets/airstream-gen-3-laminar-flow-clean-benches-vertical-stainless-steel-side-wall/LVS/	MX	N/A	N/A	Stainless Steel 316L	Clean Air	ISO Class 3 Workzone	N/A	N/A	900 x 700	N/A	N/A	N/A	1	0	ESCO Mirco (M) Sdn. Bhd	N/A	N/A	N/A	N/A		N/A
mMx	57	Mixing Vessel	Pharmafood Engineering	Mixing Vessel 13,000 L	A170810-PR-CA-001 rev: B	PCSMS	PTFE/EPDM/ any USP Class 6	ASME SEC. VIII. DIV.1	Stainless Steel 316L	4 / - 1 bar Vacuum @ 150 Celcius	Mixer Installed	Pneumatically Actuated Tank bottom outlet valve	Stainless Steel 316L	ID 2500 x SL 2440	3 side lugs support	Ra < 0-.5 uM	Diaphragm EPDM/PTFE	1	1	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A		Y
mSy	58	Storage Vessel	Pharmafood Engineering	Storage Vessel 13,000 L	A170810-PR-GA-002 rev:A	PCSTOR	PTFE/EPDM/ any USP Class 7	ASME SEC. VIII. DIV.2	Stainless Steel 316L	3 / - 1 bar Vacuum @ 150 Celcius	No Mixer Installed	Pneumatically Actuated Tank bottom outlet valve	Stainless Steel 316L	ID 2500 x SL 2438	3 leg support with 3 leg support bracing	Ra < 0-.5 uM	Diaphragm EPDM/PTFE	1	1	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A	Y
mTI	59	Temperature probe with Thermowell (Thermowell fabricated by JJK)	Endress+Hauser	Omnigrad T TR24	https://www.endress.com/en/Field-instruments-overview/Temperature-measurement-thermometers-transmitters/Pt100-thermometer-modular-design-TR24	EMV1	N/A	N/A	Thermowell: Stainless Steel 316L	-200 °C / 600 °C	PT 100 sensing element	4 - 20 mA output signal	Thermowell: Stainless Steel 316L	NPT 1/2"	Welded	Ra < 0-.5 uM	N/A	Thermowell: TRUE / Temperature: FALSE	Thermowell: TRUE / Temperature: FALSE	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	N/A		N/A	Y	Y
mSSP	60	Signal splitter	Amelec	ADM221X RTD	S:\Projects\Projects17\A170810 - MPI SMS\05. Detailed Design\04. Working Documents\MPI.SMS\Quotations & PO\Data Sheets		N/A	N/A	N/A	To split 1 incoming PT100 input into 2 Output Signals	Output 1: RTD / Output 2: 4-20mA	Supply voltage: 24Vdc / 115Vac / 230Vac	N/A	Enclosure: 50w x 75h x 110d	Din rail / Surface (optional Panel Mount)	N/A	N/A	0	0	Amelec	N/A	N/A	N/A	N/A	To split 1 incoming PT100 input into: / Output 1: RTD / Output 2: 4-20mA	N/A
mBAV7	61	Ball Valve 2" (manual)	Meca INOX	PS4LBWNI	http://www.meca-inox.com/site2016/wp-content/themes/glissando/downloads/catalogue%20V15%20FR-GB%202015_link.pdf	EMC5	PTFE/EPDM/USP Class 6/FDA approved material	ASTM	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	N/A	Manually Operated with no feed back	Valve Body: SS 316L / Ball: SS316L	2"	Buttweld	N/A	PTFE/EPDM/USP Class 6/FDA approved material	1	0	Doctrine Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	TFM 1600	N/A		N/A
mDV7	62	Shutoff valve for 1 inch pipe, triclamp, manual valve	Millipore	Valve: NA25/311-212 / Actuator: FA25/154 / Diaphragm: NA25/22		MX / SY	EPDM	ASME	Stainless Steel 316L	Press. 3 bar, Temp 160 degC	N/A	N/A	Stainless Steel 316L	1"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	1	Merck	SS 316L/1.4435	Ra ≤ 0.5 uM	EPDM/PTFE	Diaphragm Seals		N/A
mFXH	63	2" Flexible Hose for PW/WFI/PS Vessel Inlet (Hansen Coupling)	Dockweiler			MX / SY	PTFE/EPDM/ any USP Class 7	USP/FDA	Hose: Silicon/PTFE/EPDM	4 / - 1 bar Vacuum @ 150 Celcius	N/A	with female hansen coupling connected at each end	Silicon/PTFE/EPDM	2"	Ferrule Clamp Ends of Hose Modified with Hansen Coupling	Ra ≤ 0.5 uM	N/A	1	Coupling: TRUE	JJK Engineering	SS 316L/1.4435/EPDM/PTFE	Ra ≤ 0.5 uM	N/A	Hose		N/A
mFXH1	64	2" Flexible Hose for Mixing Vessel Outlet (Ferrule Clamp)	Dockweiler			MX	PTFE/EPDM/ any USP Class 7	USP/FDA	Hose: Silicon/PTFE/EPDM	4 / - 1 bar Vacuum @ 150 Celcius	N/A	Ferrule Clamp	Silicon/PTFE/EPDM	2"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	Ferrule: TRUE	JJK Engineering	SS 316L/1.4435/EPDM/PTFE	Ra ≤ 0.5 uM	N/A	Hose		N/A
mFXH2	65	1" Flexible Hose (Ferrule Clamp)	Dockweiler			MX	PTFE/EPDM/ any USP Class 7	USP/FDA	Hose: Silicon/PTFE/EPDM	4 / - 1 bar Vacuum @ 150 Celcius	N/A	Ferrule Clamp	Silicon/PTFE/EPDM	1"	Ferrule (Tri-Clamp)	Ra ≤ 0.5 uM	N/A	1	Ferrule: TRUE	JJK Engineering	SS 316L/1.4435/EPDM/PTFE	Ra ≤ 0.5 uM	N/A	Hose		N/A
mHEX	66	Heat Exchanger	Allegheny Bradford Corporation	Shell & Tube Heat Exchanger / Shell (Chilled Water): 34,100 kg/hr / Tube (Process Water): 2,850 kh/hr	C:\Users\sin.khc\Documents\datasource\MPI\Specification\Heat Exchanger	MX	Shell: EPDM O-ring / Tube: EPDM O-ring	ASME	Stainless Steel 316L	Shell Side: 4 bar @ 10 Celcius / Tube Side: 4 bar @ 80 Celcius	Process Side Cooling from 80 Celcius to 20 Celcius	N/A	Tube Side: 316L	N/A	Shell Side: Flange / Tube Side: Ferrule (Tri-Clamp)	Tube Side: Ra ≤ 0.5 uM	N/A	Tube side: TRUE	Tube Side: TRUE	JJK Engineering	SS 316L/1.4435	Ra ≤ 0.5 uM	N/A	Gaskets		N/A

## tblSafety
				0
				Effect Description	M1 Agitator	M1 Vent line drain valve	M1 Vent Valve	M1 HP CA Supply Valve	M1 LP CA Supply Valve	M1 Vacuum valve	M1 PS Supply for WFI Loop	M1 WFI Supply Valve	M1 PW Supply Valve	M1 PS Supply for PW Loop	Mx Vacuum Pump	S1 Vent line drain valve	S1 Vent Valve	S1 HP CA Supply Valve	S1 LP CA Supply Valve	S1 Vacuum valve	S1 Pressure Control	S1 PS Supply for WFI Loop	S1 WFI Supply Valve	S1 PW Supply Valve	S1 PS Supply for PW Loop	Sy Vacuum Pump	M1 Vent Filter AF1101 Drain valve	M1 Electric Heating Element	S1 Vent Filter AF3101 Drain valve	S1 Electric Heating Element	M1 Mass Indicator	Manufacturing Filtration Line Cooling Water Supply Valve	Manufacturing Filtration Line Cooling Water Return Valve	Manufacturing Filtration Line Cooling Water Supply Drain Valve	Manufacturing Filtration Line Cooling Water Return Drain Valve	Manufacturing Filtration Line cooling water supply valve	Manufacturing Filtration Line Inline Heat Exchanger Temperature Control	M1 Outlet Valve	M1 Spray Ball 1 Valve	M1 Spray Ball 2 Valve	S1 Outlet Valve	S1 Spray Ball 1 Valve	S1 Spray Ball 2 Valve	M1 SIP Condensate Drain Valve	M1 CIP Drain Valve	M1 Drain Temperature Indicator	SMFL1 Filtration Line filter outlet drain valve	SMFL1 Filtration Line filter outlet valve	SMFL1 Filtration Line outlet Flowpath Indicator	SMFL1 Filtration Outlet CIP & SIP Flowpath Indicator	SMFL1 M1 to S1/S3/FL1 Flowpath Indicator	SMFL1 M1 to S2/S4/FL2 Flowpath Indicator	SMFL1 Filtration Line SIP Condenste Drain Valve	SMFL1 Filtration Line CIP Drain Valve	SMFL1 Drain Temperature Indicator	MMFL1 Filtration Line filter inlet drain valve	MMFL1 Inline Heat Exchanger inlet valve	MMFL1 Filtration Inlet Flowpath Indicator	MMFL1 Filtration Inlet CIP & SIP Flowpath Indicator	S1 SIP Drain valve	S1 CIP Drain valve	S1 Drain temperature	S1 Transfer line Valve Matrix	S1 Transfer line Valve Matrix	S1 Transfer line Valve Matrix	S1 Transfer line Valve Matrix	S1 M1/M2 to S1/FM1 Flowpath Indicator	M1 Pressure Control
	Test Method: / Interlocks have already been verified as part of Software Module Testing. This document may be used during OQ execution to perform testing of interlocks as they are encounted. / To record a result, highlight each interlock box with a red border when an interlock is encountered.					Class	SIC1	POS4	POS4	POS4	POS4	POS4	POS4	POS4	POS4	MOT1	POS4	POS4	POS4	POS4	POS4	PC1	POS4	POS4	POS4	POS4	MOT1	POS4	HE1	POS4	HE1	MI1	POS1	POS1	POS4	POS4	MOD1	TC1	POS4	POS4	POS4	POS4	POS4	POS4	POS4	POS4	TI2	POS4	POS1	ZSC2	ZSC2	ZSC2	ZSC2	POS4	POS4	TI2	POS4	POS4	ZSC2	ZSC2	POS4	POS4	TI2	POS4	POS4	POS4	POS4	ZSC2	PC1
				Target	AG1101	BAV1139	DV1101	DV1103	DV1105	DV1107	DV1109	DV1111	DV1113	DV1115	VP1000	BAV3139	DV3101	DV3103	DV3105	DV3107	PIC3103	DV3109	DV3111	DV3113	DV3115	VP3000	BAV1141	HE1101	BAV3141	HE3101	MI1101	BAV1151	BAV1153	BAV1167	BAV1169	TCV1157	TIC1109	DV1121	DV1117	DV1119	DV3121	DV3117	DV3119	BAV1143	BAV1145	TI1107	DV1135	DV1137	ZSC1109	ZSC1111	ZSC1117	ZSC1119	BAV1147	BAV1149	TI1111	DV1171	DV1173	ZSC1113	ZSC1115	BAV3143	BAV3145	TI3107	DV3123	DV3125	DV3127	DV3129	ZSC3109	PC1103
				X = Critical Interlock / M = Non-critical interlock which can be manually overridden	Action	Disabled	Close	Close	Close	Close	Close	Close	Close	Close	Disabled	Close	Close	Close	Close	Close	Disabled	Close	Close	Close	Close	Disabled	Close	Disabled	Close	Disabled	Disabled	Close	Close	Close	Close	Close	Disabled	Close	Close	Close	Close	Close	Close	Close	Close	Low Low	Close	Close	Close	Out	Out	Out	Close	Close	Low Low	Close	Close	Out	Out	Close	Close	Low Low	Close	Close	Close	Close	Out	Disabled	END
Name	Source	Class	State	Function	FunctionEnd	Interlock	Cause Description	No	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26	27	28	29	30	31	32	33	34	35	36	37	38	39	40	41	42	43	44	45	46	47	48	49	50	51	52	53	54	55	56	57	58	59	60	61	62	63	64
IL1	AG1101	SIC1	Enabled	A		#INTERLOCK;	M1 Agitator	1					X			X
IL1	BAV1139	POS4	OPENED	A (O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 Vent line drain valve	2
IL1	DV1101	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 Vent Valve	3					M	X			X
IL1	DV1103	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 HP CA Supply Valve	2					X
IL1	DV1105	POS2	OPENED	) A (O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 LP CA Supply Valve	3					X
IL1	DV1107	POS2	OPENED	O	)	(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 Vacuum valve	4				M	M		X	X	X	X
IL2	ZSC1103	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	M1 WFI Supply Flowpath Indicator	3					X	X
IL2	ZSC1107	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	M1 inlet line Flowpath Indicator	4
IL3	ZSC1105	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	M1 PW Supply Flowpath Indicator	5					X	X
IL3	ZSC1107	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	M1 inlet line Flowpath Indicator	4
IL4	DV1109	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 PS Supply for WFI Loop	5			X			X		X	X	X
IL4	DV1111	POS4	OPENED	O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 WFI Supply Valve	6			X			X	X		X	X
IL4	DV1113	POS4	OPENED	O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 PW Supply Valve	5			X			X	X	X		X
IL4	DV1115	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	M1 PS Supply for PW Loop	6			X			X	X	X	X
IL4	BAV3139	POS4	OPENED	O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 Vent line drain valve	7
IL4	DV3101	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 Vent Valve	6					M		X			X
IL5	ZSC3103	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 WFI Supply Flowpath Indicator	7					X	X
IL5	ZSC3107	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 Inlet line Flowpath Indicator	8
IL6	ZSC3105	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 PW Supply Flowpath Indicator	7					X	X
IL6	ZSC3107	ZSC2	Out	O		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 Inlet line Flowpath Indicator	8
IL7	DV3103	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 HP CA Supply Valve	9					X
IL7	DV3105	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 LP CA Supply Valve	8					X
IL7	DV3107	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 Vacuum valve	9					M	M			X	X	X	X
IL7	PC3103	PC1	Enabled	O		#INTERLOCK;	S1 Pressure Control	10
IL7	DV3109	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 PS Supply for WFI Loop	9					X			X			X	X	X
IL7	DV3111	POS4	OPENED	O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 WFI Supply Valve	10					X			X		X		X	X
IL7	DV3113	POS4	OPENED	O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 PW Supply Valve	11					X			X		X	X		X
IL7	DV3115	POS2	OPENED	O		(; / L "idbPOS2".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	S1 PS Supply for PW Loop	10					X			X		X	X	X
IL8	ZSC1113	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	MMFL1 Filtration Inlet Flowpath Indicator	11					X	X
IL8	ZSC1115	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	MMFL1 Filtration Inlet CIP & SIP Flowpath Indicator	12
IL9	ZSC1115	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	MMFL1 Filtration Inlet CIP & SIP Flowpath Indicator	11					X
IL10	ZSC1109	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 Filtration Line outlet Flowpath Indicator	12					X	X
IL10	ZSC1111	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 Filtration Outlet CIP & SIP Flowpath Indicator	13
IL21	ZSC3111	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 to S1/BFS1 Flowpath Indicator	12					X
IIL21	ZSC3113	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL2 to S1/BFS1 Flowpath Indicator	13
IL22	ZSC3111	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 to S1/BFS1 Flowpath Indicator	14					X
IL22	ZSC4113	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 to S2/BFS2 Flowpath Indicator	13
IL23	ZSC3111	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 to S1/BFS1 Flowpath Indicator	14					X					X
IL23	ZSC3113	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL2 to S1/BFS1 Flowpath Indicator	15
IL23	ZSC4113	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 to S2/BFS2 Flowpath Indicator	14
IL24	ZSC3115	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 to F1P1 Flowpath Indicator	15					X
IL24	ZSC3117	ZSC2	Out	A		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 to F2P1 Flowpath Indicator	16
IL25	ZSC1101	ZSC1	Out	A		"idbZSC1".@@INSTANCE@@.DI_PV;	M1 Manway Close Indicator	15	M			X	X	M	X	X	X	X
IL26	ZSC3101	ZSC1	Out	A		"idbZSC1".@@INSTANCE@@.DI_PV;	S1 Manway Close Indicator	16					X	X	M		X	X	X	X
IL27	BAV1167	POS4	OPENED	A(O		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	Manufacturing Filtration Line Cooling Water Supply Drain Valve	17					X	X			X	X
IL27	BAV1169	POS4	OPENED	O)		(; / L "idbPOS4".@@INSTANCE@@.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.@@STATE@@; / ==I; / );	Manufacturing Filtration Line Cooling Water Return Drain Valve	16
IL28	ES1100	DI1	Enabled	A(O		"idbDI1".@@INSTANCE@@.DI_PV;	M1 Emergency Stop	17	X	X	X	X	X	X	X	X					X	X			X	X	X	X	X	X		X	X	X				X	X		X	X					X	X		X	X					X
IL28	ES1101	DI1	Enabled	O)		"idbDI1".@@INSTANCE@@.DI_PV;	M1 Emergency Stop mounted on M1/M2 Shared HMI	18
IL29	ES3100	DI1	Enabled	A		"idbDI1".@@INSTANCE@@.DI_PV;	S1 Emergency Stop	17					X	X	X	X	X	X	X	X				X	X					X	X	X					X	X		X	X	X	X
IL30	PB74101	DI2	Enabled	A		"idbDI2".@@INSTANCE@@.DI_PV;	BFS1 Pause Push Button	18					X
IL31	PI1103	PI1	High High	A		#INTERLOCK;	M1 Vessel Pressure	19	M	X	X	X	X	X	X	X	X					X	X			X	X	X	X	X	X	X	X				X	X		X	X	X	X	X	X	X	X		X	X
IL32	PI3103	PI1	High High	A		#INTERLOCK;	S1 Vessel Pressure	18					X	X	X	X	X	X	X	X				X	X					X	X	X					X	X		X	X	X	X
IL33	MI1101	MI1	High High	A		#INTERLOCK;	M1 Mass Indicator	19	X			M	M	X	X	X	X	X
IL34	ZSC1113	ZSC2	In	A		"idbZSC2".@@INSTANCE@@.DI_PV;	MMFL1 Filtration Inlet Flowpath Indicator	20					M
IL34	ZSC1109	ZSC2	In	A		"idbZSC2".@@INSTANCE@@.DI_PV;	SMFL1 Filtration Line outlet Flowpath Indicator	19
IL34	TI1109	TI1	High High	A		#INTERLOCK;	Manufacturing Filtration Line Inline Heat Exchanger Temperature	20
IL35	ASL3000	DI1	Low Low	A		"idbDI1".@@INSTANCE@@.DI_PV;	Sy Instrument Air Switch	21					X	X	X	X	X	X	X	X				X	X					X	X	X					X	X		X	X	X	X
IL36	ASL1000	DI1	Low Low	A		"idbDI1".@@INSTANCE@@.DI_PV;	Mx Instrument Air Switch	20	X	X	X	X	X	X	X	X					X	X			X	X	X	X	X	X		X	X	X				X	X		X	X					X	X		X	X					X
IL37	TI3105	TI1	High High	A		#INTERLOCK;	S1 Temperature Indicator	21					M					M
IL37	ZSC3111	ZSC2	Out	A (O		"idbZSC2".@@INSTANCE@@.DI_PV;	VTL1 to M1 Flowpath Indicator	18
IL37	ZSC3113	ZSC2	Out	O)		"idbZSC2".@@INSTANCE@@.DI_PV;	VTL1 to M2 Flowpath Indicator	19
IL37	ZSC3115	ZSC2	In	A (O		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 to F1P1 Flowpath Indicator	20
IL37	ZSC3117	ZSC2	In	O)		"idbZSC2".@@INSTANCE@@.DI_PV;	S1 to F2P1 Flowpath Indicator	19

## tblClass_Requirement
Level	ClassID	Class	Type	ReqOrder	ReqRef	Requirement
CM	15	DI1	Scope	0		Applies to all digital input alarms throughout the Solution Manufacturing and Filling Systems. / This CM is similar to the manway closed indication ZSC1 except this CM does not provide for alarm cutout and has different state names.
CM	15	DI1	Req	1	F1	This CM shall indicate healthy if the digital input signal is ON.
CM	15	DI1	Req	2	F2	This CM shall raise an interlock condition if the digital input signal is OFF.
CM	15	DI1	Req	3	F3	This CM shall raise an alarm message if the digital input signal is OFF.
CM	15	DI1	Req	4	F4	The signal from the field shall be fail-safe (i.e. always ON and any loop fault will generally cause the digital input to also go OFF).
CM	15	DI1	Req	5	F5	This CM shall be used for the following types of field devices:
CM	15	DI1	Req	6	F6	1. Manufacturing and Storage Vessels Bursting Disc
CM	15	DI1	Req	7	F7	2. Plant Emergency Stop
CM	15	DI1	Req	8	F8	3. Instrument Air Pressure Switch
CM	16	DI2	Scope	0		Applies to all digital input alarms throughout the Solution Manufacturing and Filling Systems which do not have a physical input from the field.
CM	16	DI2	Req	1	F1	This CM shall indicate healthy if the software signal state is ON.
CM	16	DI2	Req	2	F2	This CM shall raise an interlock condition if the software signal state is OFF.
CM	16	DI2	Req	3	F3	This CM shall raise an alarm message if the software signal state is OFF.
CM	16	DI2	Req	4	F4	This CM shall be used for Filling Suite Pause Push Button.
CM	17	HE1	Scope	0		Applies to all Manufacturing Vessels and Storage Vessels located in Solution Manufacturing System SMS1.
CM	17	HE1	Req	1	F1	The heating element of the filter can be switched on or off. It will normally be left on all the time.
CM	17	HE1	Req	2	F2	When switched on, the heater prevents condensation inside the gas filter housing.
CM	18	MI1	Scope	0		Applies to the Manufacturing Vessels M1 and M2.
CM	18	MI1	Req	1	F1	This CM is for indicating the mass of the manufacturing vessels.
CM	18	MI1	Req	2	F2	The input for the measured mass shall be scaled from Low Limit 0 kg to High Limit 13,000 kg
CM	18	MI1	Req	3	F3	A high high mass interlock shall close all gas and liquid supply to the vessel to protect the operator from potentially unsafe plant conditions and the load cells being overloaded.
CM	18	MI1	Req	4	F4	A high high mass alarm shall be raised to alert the operator in the event of the high high mass interlock being reached.
CM	18	MI1	Req	5	F5	A high mass alarm shall also be set to warn of an impending high high condition. The interlock and alarm values are equipment based and will not change based on the process recipe.
CM	18	MI1	Req	6	F6	The CM shall check the quality of the analog input signal and indicate bad Data Quality when the I/O signal is bad.
CM	18	MI1	Req	7	F7	A bad Data Quality I/O signal shall also interlock all gas and liquid supply to the vessel (in this case the actual vessel mass is not known and could be high high).
CM	19	MOD1	Scope	0		Applies to the pneumatically actuated modulating control valve on the chilled water inlet to the heat exchanger.
CM	19	MOD1	Req	1	F1	The analog signal to modulate the control valve shall either be received from the temperature controller module TC1 or from a locally set fixed value.
CM	19	MOD1	Req	2	F2	Control shall be enabled by turning on the digital output to open the solenoid valve in the air supply line to the control valve.
CM	20	MOT1	Scope	0		There are two vacuum pumps, one serving the Manufacturing vessels and pipework and one serving the Storage vessels and pipework.
CM	20	MOT1	Req	1	F1	The vacuum pump motor is provided with a DOL starter with the following signals: / a) Run command output signal
CM	20	MOT1	Req	2	F2	b) Motor overload trip input signal
CM	20	MOT1	Req	3	F3	c) Motor running input signal
CM	22	PC1	Scope	0		Applies to simple on/off control strategy for the injection of compressed air into each of the manufacturing and storage vessels.
CM	22	PC1	Req	1	F1	Opens the pre-selected low pressure or high pressure compressed air supply valve if the actual vessel pressure is less than a pre-defined amount below a setpoint value.
CM	22	PC1	Req	2	F2	Opens the pre-selected low pressure or high pressure compressed air supply valve if the vessel pressure reaches the setpoint value.
CM	22	PC1	Req	3	F3	Opens the vent valve if the actual vessel pressure is greater than a pre-defined amount above the setpoint value.
CM	22	PC1	Req	4	F4	Closes the vent valve if the vessel pressure reaches the setpoint value.
CM	22	PC1	Req	5	F5	Indicates the pressure inside the vessel.
CM	22	PC1	Req	6	F6	The input for the measured pressure shall be scaled from Low Limit -1 bar to High Limit 5 bar.
CM	22	PC1	Req	7	F7	High high pressure interlock shall close compressed air and liquid supply to the vessel to protect the operator from unusually high pressure and potentially unsafe plant conditions.
CM	22	PC1	Req	8	F8	High high pressure interlock value shall be set below the bursting disc pressure rating to protect the disc.
CM	22	PC1	Req	9	F9	High high pressure alarm shall be raised to alert the operator in the event of the high high pressure interlock being reached.
CM	22	PC1	Req	10	F10	Low low pressure alarm shall also be raised to alert the operator of unusually low pressure and potentially unsafe plant conditions.
CM	22	PC1	Req	11	F11	Additionally other low and high pressure alarms shall also be able to be set to warn of an impending low low or high high condition. / Interlock and alarm values are equipment based and will not change based on the process recipe.
CM	22	PC1	Req	12	F12	Quality of the analog input signal shall be checked and shall indicate bad Data Quality when the I/O signal is bad.
CM	22	PC1	Req	13	F13	Bad Data Quality I/O signal shall also interlock compressed air and liquid supply to the vessel (in case the actual vessel pressure is not known and could be high high).
CM	22	PC1	Req	14	F14	Provision shall be made to be able to enable or disable the following alarms only: / a) Low alarm
CM	22	PC1	Req	15	F15	b) Low low alarm
CM	21	PI1	Scope	0		Applies to vessel pressure indicator in each of the manufacturing and storage vessels.
CM	21	PI1	Req	1	F1	A high high pressure interlock shall close all gas and liquid supply to the vessel to protect the operator from unusually high temperature and pressure and potentially unsafe plant conditions.
CM	21	PI1	Req	2	F2	A high high pressure alarm shall be raised to alert the operator in the event of the high high pressure interlock being reached.
CM	21	PI1	Req	3	F3	Low and high pressure alarm values shall be process recipe-based and shall be able to be changed based on the process recipe.
CM	21	PI1	Req	4	F4	The low and high alarms shall also be able to be enabled and disabled based on the process recipe.
CM	21	PI1	Req	5	F5	The CM shall check the quality of the analog input signal and indicate bad Data Quality when the I/O signal is bad.
CM	21	PI1	Req	6	F6	A bad Data Quality I/O signal shall also interlock all gas and liquid supply to the vessel (in this case the actual vessel temperature is not known and could be high high).
CM	23	POS1	Scope	0		Applies to a pneumatically actuated on/off valve which has one digital output to command the valve to open or close with no position feedback.
CM	23	POS1	Req	1	F1	This CM is for a normally closed, solenoid operated, pneumatic on/off valve with one digital output which commands the valve to open or close.
CM	23	POS1	Req	2	F2	No position feedback signals required.
CM	26	POS4	Scope	0		Applies to all pneumatic on/off valves with both opened and closed position feedback.
CM	26	POS4	Req	1	F1	The CM has one digital output which commands the valve to open or close.
CM	26	POS4	Req	2	F2	An opened position feedback proximity switch shall provide a digital input for assurance that the valve is fully opened.
CM	26	POS4	Req	3	F3	A closed position feedback proximity switch shall provide a digital input for assurance that the valve is fully closed and isolating.
CM	26	POS4	Req	4	F4	A timer shall be used to monitor valve performance and indicate a fault if the valve is commanded to open but does not reach the opened position or commanded to close but does not reach the closed position within a pre-defined time out period.
CM	27	SIC1	Scope	0		Applies to the Manufacturing Vessel agitator motor.
CM	27	SIC1	Req	1	F1	This CM is for the output control of the Manufacturing Vessel agitator motor to a speed setpoint.
CM	27	SIC1	Req	2	F2	The range for the analog inputs and outputs to the stirrer motor shall be scaled from 0 to 250 rpm.
CM	27	SIC1	Req	3	F3	Can be enabled at any time however the motor run command shall only be issued to the field when the mass in the vessel is above a predefined minimum amount.
CM	27	SIC1	Req	4	F4	Hysteresis shall be applied to the vessel mass at which the motor can run to prevent hunting if the load cell signal becomes erratic when the motor is turned on.
CM	27	SIC1	Req	5	F5	In manual mode, the minimum vessel mass condition shall be overridden and the motor shall run whenever the agitator is enabled, regardless of the level in the vessel.
CM	28	TC1	Scope	0		Applies to heat exchanger in Solution Manufacturing System.
CM	28	TC1	Req	1	F1	This CM is for PID-controlled cooling in the heat exhanger.
CM	29	TI1	Scope	0		Applies to all Manufacturing and Storage Vessels.
CM	29	TI1	Req	1	F1	This CM is for indicating the temperature inside manufacturing and storage vessels.
CM	29	TI1	Req	2	F2	The input for the measured temperature shall be scaled from Low Limit: 0°C to High Limit: 150°C.
CM	29	TI1	Req	3	F3	A high high temperature interlock shall close all gas and liquid supply to the vessel to protect the operator from unusually high temperature and pressure and potentially unsafe plant conditions.
CM	29	TI1	Req	4	F4	A high high temperature alarm shall be raised to alert the operator in the event of the high high temperature interlock being reached.
CM	29	TI1	Req	5	F5	A low low temperature alarm shall also be raised to alert the operator of unusually low temperature and potentially unsafe plant conditions. / The interlock and low low and high high alarm values are equipment-based and will not change based on the process recipe.
CM	29	TI1	Req	6	F6	Additionally other low and high temperature alarms shall also be able to be set.
CM	29	TI1	Req	7	F7	The low and high alarm values shall be process recipe-based and shall be able to be changed based on the process recipe.
CM	29	TI1	Req	8	F8	The low and high alarms shall also be able to be enabled and disabled based on the process recipe.
CM	29	TI1	Req	9	F9	The CM shall check the quality of the analog input signal and indicate bad Data Quality when the I/O signal is bad.
CM	29	TI1	Req	10	F10	A bad Data Quality I/O signal shall also interlock all gas and liquid supply to the vessel (in this case the actual vessel temperature is not known and could be high high).
CM	30	TI2	Scope	0		Applies to pipework mounted temperature indicators in the Solution Manufacturing Systems.
CM	30	TI2	Req	1	F1	This CM is for indicating the temperature in the line.
CM	30	TI2	Req	2	F2	The input for the measured temperature shall be scaled from Low Limit 0°C to High Limit: 150°C.
CM	30	TI2	Req	3	F3	The CM shall provide for the following alarms, which shall be able to be individually enabled or disabled: / a) High high temperature.
CM	30	TI2	Req	4	F4	b) High temperature.
CM	30	TI2	Req	5	F5	c) Low temperature.
CM	30	TI2	Req	6	F6	d) Low low temperature.
CM	30	TI2	Req	7	F7	The CM shall check the quality of the analog input signal and indicate bad Data Quality when the I/O signal is bad.
CM	31	ZSC1	Scope	0		Applies to all vessels manway position closed indication switch throughout the Solution Manufacturing Systems. This CM is similar to the digital input fault indication DI1 except this CM allows alarm cutout whereas DI1 does not. Also the states for this CM have different names. / The manway cover is required to be closed: / a) When charging the vessel with water or gas, both of which may be a potential danger to the operator. / b) When maintaining a sterile environment in the vessel.
CM	31	ZSC1	Req	1	F1	This CM shall indicate healthy and CLOSED if the digital input signal is ON.
CM	31	ZSC1	Req	2	F2	This CM shall raise an interlock condition if the digital input signal is OFF (i.e. the manway cover is OPENED).
CM	31	ZSC1	Req	3	F3	This CM shall raise an alarm message if the digital input signal is OFF when the alarm cutout flag is not set.
CM	31	ZSC1	Req	4	F4	When the alarm cutout flag is set the alarm message shall not be raised even if the digital input signal is OFF.
CM	31	ZSC1	Req	5	F5	The signal from the field shall be fail-safe (i.e. always ON and any loop fault will generally cause the digital input to also go OFF).
CM	32	ZSC2	Scope	0		Applies to all manual flowpath devices such as spoolpieces and flowplates throughout the Solution Manufacturing Systems.
CM	32	ZSC2	Req	1	F1	This CM shall indicate whether a manual flowpath device is IN or OUT.
CM	32	ZSC2	Req	2	F2	The system shall indicate when the manual flowpath device REQUIRED state does not match the actual state. This should not raise an alarm but the operator needs to be alerted that manual action is required. / It is left to manual plant procedures to ensure that when a device is placed into position and the feedback switch is made that the device is properly secured and sealed. The switch feedback cannot guarantee the device is physically clamped.
EM	33	EMA1	Scope	0		Applies to the vessel agitator in manufacturing vessel M1 in Solution Manufacturing System SMS1 and vessels M2 in SMS 2.
EM	33	EMA1	Req	1	F1	Agitator shall run with a preset speed setpoint.
EM	33	EMA1	Req	2	F2	The agitator shall be able to be run for a limited time only to prevent it being inadvertently left enabled.
EM	33	EMA1	Req	3	F3	The timeout period shall be configurable.
EM	33	EMA1	Req	4	F4	The EM shall be able to be stopped at any time even if the timeout period has not yet expired.
EM	33	EMA1	Req	5	F5	The EM shall not provide the option to the operator to run the agitator without a time out period having been set.
EM	34	EMC1	Scope	0		Applies to the compressed air, vent and vacuum lines of each manufacturing and storage vessel.
EM	34	EMC1	Req	1	F1	The EM shall be able to be run in an On/Off Pressure Control state to pressurise the vessel head space with either HPCA or LPCA to a predefined pressure setpoint until commanded to stop.
EM	34	EMC1	Req	2	F2	In the Pressure Control state the vessel head space pressure shall be maintained between low and high hysteresis values.
EM	34	EMC1	Req	3	F3	In the Pressure Control state the vent valve shall open to relieve high pressure above the high hysteresis value and close again when the pressure drops below the target pressure setpoint.
EM	34	EMC1	Req	4	F4	In the Pressure Control state the selected gas supply valve shall open to increase pressure when below the low hysteresis value and close again when the pressure rises above the target pressure setpoint.
EM	34	EMC1	Req	5	F5	In the pressure control state there shall be a timeout and alarm if the pressure does not reach the setpoint within a certain time period.
EM	34	EMC1	Req	6	F6	The EM shall be able to run in a valve fully opened state which which bypasses the pressure controller and simply opens the selected gas inlet valve to provide maximum supply pressure to the vessel until commanded to stop.
EM	34	EMC1	Req	7	F7	The EM shall be able to vent the vessel by opening the vent valve until commanded to close.
EM	34	EMC1	Req	8	F8	The EM shall be able to evacuate the vessel via the vacuum pump until commanded to stop.
EM	34	EMC1	Req	9	F9	The drain line steam trap valve shall be able to be opened during SIP.
EM	35	EMC2	Scope	0		Applies to the WFI, PW and PS supply system to the Manufacturing vessel M1 and M2.
EM	35	EMC2	Req	1	F1	The EM shall charge PW or WFI to a predefined mass endpoint.
EM	35	EMC2	Req	2	F2	The EM shall flush any of PW, PS(PW), WFI or PS(WFI) for a predefined time.
EM	35	EMC2	Req	3	F3	The EM shall flush any of PW, PS(PW), WFI or PS(WFI) indefinitely until commanded to stop.
EM	35	EMC2	Req	4	F4	The EM shall be able to have the operator setup the manual hose connection flowpath for the required addition prior to charging or flushing with steam or water.
EM	35	EMC2	Req	5	F5	Once the flowpath is setup, low level interlocks shall continue to monitor the position of the manual hose connection and asynchronously close all steam and water supply valves should the flowpath no longer be integral.
EM	35	EMC2	Req	6	F6	The EM shall be able to have the operator isolate the water and steam inlet manifold from the vessel by ensuring the flowpath proximity switches are not in place.
EM	35	EMC2	Req	7	F7	There shall be a time-out alarm when charging to a predefined mass endpoint if the mass in the vessel does not increase within a reasonable time period.
EM	36	EMC3	Scope	0		Applies to Storage vessels S1, S2, S3 and S4. / This EM class is similar to EMC2 except the storage vessels do not have load cells and hence there can be no charging to a mass endpoint.
EM	36	EMC3	Req	1	F1	The EM shall flush any of PW, PS(PW), WFI or PS(WFI) for a predefined time.
EM	36	EMC3	Req	2	F2	The EM shall flush any of PW, PS(PW), WFI or PS(WFI) indefinitely until commanded to stop.
EM	36	EMC3	Req	3	F3	The EM shall be able to have the operator setup the manual hose connection flowpath for the required addition prior to charging or flushing with steam or water.
EM	36	EMC3	Req	4	F4	Once the flowpath is setup, low level interlocks shall continue to monitor the position of the manual hose connection and asynchronously close all steam and water supply valves should the flowpath no longer be integral.
EM	36	EMC3	Req	5	F5	The EM shall be able to have the operator isolate the water and steam inlet manifold from the vessel by ensuring the flowpath proximity switches are not in place.
EM	37	EMC5	Scope	0		Applies to the vacuum pump systems. One vacuum system is shared between the manufacturing vessels M1 and M2 and another vacuum system is shared betweeen the storage vessels S1, S2, S3 and S4. Each vacuum system comprises 2 vacuum pumps which always run together.
EM	37	EMC5	Req	1	F1	The EM shall monitor the vessel vacuum valves and start the vacuum pump if any valve opens, indicating a consumer call for vaccum.
EM	38	EMG1	Scope	0		Applies to all manufacturing and storage vessels.
EM	38	EMG1	Req	1	F1	Filter state, which is the normal operational state of the EM. In this state the SIP condensate line valve shall be closed.
EM	38	EMG1	Req	2	F2	SIP state, in which the SIP condensate line valve shall be opened.
EM	38	EMG1	Req	3	F3	In both states the filter housing heater element shall only turn on when the vessel temperature is above a preset value.
EM	38	EMG1	Req	4	F4	Once the vessel temperature drops below that value less a deadband parameter the heater shall be turned off a set time later.
EM	39	EMM1	Scope	0		Applies to the load cells in the manufacturing vessels M1 and M2.
EM	39	EMM1	Req	1	F1	Provides a more accurate measurement of the vessel mass by allowing it to settle without agitation.
EM	39	EMM1	Req	2	F2	Users of the vessel mass shall first check the EM Substate completion flag before using the measured value provided by the EM.
EM	39	EMM1	Req	3	F3	Current mass (measured value from MI1 CM). This is the same as the Gross mass.
EM	39	EMM1	Req	4	F4	Tare mass (MI1 value saved when vessel empty).
EM	39	EMM1	Req	5	F5	Net mass (Current mass – Tare mass).
EM	40	EMS1	Scope	0		Unit Emergency stop placeholder EM.
EM	40	EMS1	Req	1	F1	This is an S88 placeholder only. The E-Stop DI1 CM shall be interlocked with all functions and hardwired with all associated motors.
EM	41	EMT1	Scope	0		Applies to Manufacturing Filtration Line heat exchanger cooling control.
EM	41	EMT1	Req	1	F1	Perform PID controlled cooling of the filtration line heat exhanger to a defined product temperature setpoint measured in the filtration line at the outlet of the heat exchanger.
EM	41	EMT1	Req	2	F2	Perform pre-cooling of the heat exchanger prior to product flow through it. In this case cooling is achieved by setting the cooling water temperature control valve to its fixed output position.
EM	42	EMV1	Scope	0		Applies to all vessels in SMS1 and SMS2.
EM	42	EMV1	Req	1	F1	The EM shall discharge the vessel contents by opening the bottom outlet valve.
EM	42	EMV1	Req	2	F2	The EM shall be able to disable the manway cover alarm so that the manway cover may be opened or closed by the operator without alarm for filling the vessel with solid compounds during batch manufacture. The alarm may be re-enabled after batch operations are complete.
EM	42	EMV1	Req	3	F3	The EM shall also provide state of the manway proximity switch.
EM	42	EMV1	Req	4	F4	The EM shall also provide the state of the vessel overpressure bursting disc.
EM	43	EMV2	Scope	0		Applies to all vessels in SMS1 and SMS2 and includes only the inlet spray ball valves.
EM	43	EMV2	Req	1	F1	The EM shall allow the two spray ball inlet valve on the top of each vessel to either both be opened, both be closed or operate in a "flip-flop" mode where each valve alternately opens and closes so that only one valve is opened at a time.
EM	44	EMX1	Scope	0		Applies to Manufacturing vessels M1 and M2 filtration lines.
EM	44	EMX1	Req	1	F1	The EM shall transfer product from manufacturing vessel to the filter manufacturing filtration line.
EM	44	EMX1	Req	2	F2	The EM shall CIP filtration transfer line from manufacturing vessel to CIP Wash Drain tundish.
EM	44	EMX1	Req	3	F3	The EM shall SIP filtration transfer line from manufacturing vessel.
EM	44	EMX1	Req	4	F4	The EM shall also make drain line SIP condensate temperature available to other user and/or other users can also access the CMs for these devices
EM	44	EMX1	Req	5	F5	The EM shall indicate that the flowpath is setup correctly for the selected duty and shall provide an interlock flag for monitoring by other agents, such as the Unit.
EM	44	EMX1	Req	6	F6	The flowpath interlock flag shall only be raised when a separate Interlock Armed flag is set, indicating that the flow path is now critical to product and operator safety. The Armed flag shall be set by a sequence once initial setup of the flowpath has been confirmed.
EM	45	EMX2	Scope	0		Applies to Storage vessels S1, S2, S3 and S4.
EM	45	EMX2	Req	1	F1	The EM shall be configured for the transfer path from manufacturing vessel to storage vessel via the heat exchanger and manufacturing filtration line. Both for product transfers as well as CIP and SIP.
EM	45	EMX2	Req	2	F2	The EM shall be configured for transfer path from a storage vessel to filling line 1 or filling line 2.
EM	45	EMX2	Req	3	F3	The EM shall be configured for transfer path to filling line 1 or filling line 2 directly from a manufacturing vessel.
EM	45	EMX2	Req	4	F4	The EM shall configure SIP path with all valves opened.
EM	45	EMX2	Req	5	F5	The EM shall post SIP CA pressurisation state where the terminal path valves are closed but other valves remain opened.
EM	45	EMX2	Req	6	F6	Setup of the flow path for SIP shall also be used in the filtration operation as the flow path is the same.
EM	45	EMX2	Req	7	F7	The EM shall also make sterile filter outlet pressure available to other user and/or other users can also access the CMs for these devices
EM	45	EMX2	Req	8	F8	The EM shall indicate that the flowpath is setup correctly for the selected duty and shall provide an interlock flag for monitoring by other agents, such as the Unit.
EM	45	EMX2	Req	9	F9	The flowpath interlock flag shall only be raised when a separate Interlock Armed flag is set, indicating that the flow path is now critical to product and operator safety. The Armed flag shall be set by a sequence once initial setup of the flowpath has been confirmed.
EM	46	EMX4	Scope	0		Applies to the arrangement of CIP and SIP drains throughout the manufacturing and filling systems.
EM	46	EMX4	Req	1	F1	The EM shall arrange the valves for CIP, with the CIP drain valve opened and SIP drain valve closed.
EM	46	EMX4	Req	2	F2	The EM shall arrange the valves for SIP, with the CIP drain valve closed and SIP drain valve opened.
EM	46	EMX4	Req	3	F3	The EM shall also make drain line SIP condensate temperature available.
EM	46	EMX4	Req	4	F4	The SIP drain valve shall have a pulse mode which periodically pulses the valve open and closed for predetermined opened and closed times.
EM	46	EMX4	Req	5	F5	The EM shall indicate that the flowpath is setup correctly for the selected duty and shall provide an interlock flag for monitoring by other agents, such as the Unit.
EM	46	EMX4	Req	6	F6	The flowpath interlock flag shall only be raised when a separate Interlock Armed flag is set, indicating that the flow path is now critical to product and operator safety. The Armed flag shall be set by a sequence once initial setup of the flowpath has been confirmed.
EM	47	EMX5	Scope	0		Applies to the filling inlet line to the BFS machine.
EM	47	EMX5	Req	1	F1	This EM is a placeholder for the filling pause push button and filling line temperature indicator.
EM	48	EMX6	Scope	0		Applies to the storage vessel transfer line after the filters.
EM	48	EMX6	Req	1	F1	The EM shall CIP the storage vessel filtration transfer line to the CIP Wash Drain tundish.
EM	48	EMX6	Req	2	F2	The EM shall SIP the storage vessel filtration transfer line.
EM	48	EMX6	Req	3	F3	The EM shall also make drain line SIP condensate temperature available to other user and/or other users can also access the CMs for these devices
EM	48	EMX6	Req	4	F4	The EM shall indicate that the flowpath is setup correctly for the selected duty and shall provide an interlock flag for monitoring by other agents, such as the Unit.
EM	48	EMX6	Req	5	F5	The flowpath interlock flag shall only be raised when a separate Interlock Armed flag is set, indicating that the flow path is now critical to product and operator safety. The Armed flag shall be set by a sequence once initial setup of the flowpath has been confirmed.
UN	#N/A	FPZ	Scope	0		Applies to the two Blow fill seal Filling Pipes.
UN	#N/A	FPZ	Req	1	F1	The unit manages Product Filling Operations.
UN	53	MX	Scope	0		Applies to Manufacturing vessels M1 and M2.
UN	53	MX	Req	1	F1	The unit can run setup for CIP and SIP and manufacturing operations
UN	53	MX	Req	2	F2	The unit can run set up for vacuum and vacuum hold test.
UN	53	MX	Req	3	F3	The unit can run CIP.
UN	53	MX	Req	4	F4	The unit can run SIP.
UN	53	MX	Req	5	F5	The unit can run manufacture.
UN	53	MX	Req	6	F6	The unit can run cooling and filtration transfer to storage and/or direct to filling line.
UN	54	SMFL	Scope	0		Applies to the two Storage Vessel Filtration Lines for S1, S2, S3 and S4.
UN	54	SMFL	Req	1	F1	The unit can run setup for CIP and SIP and manufacturing operations
UN	54	SMFL	Req	2	F2	The unit can run CIP.
UN	54	SMFL	Req	3	F3	The unit can run SIP.
UN	54	SMFL	Req	4	F4	The unit can run filtration transfer to the BFS filling machines.
UN	55	SY	Scope	0		Applies to Storage vessels S1 and S2 and future vessels S3 and S4.
UN	55	SY	Req	1	F1	The unit can run Isolation of the vessel to protect against possible sources of contamination
UN	55	SY	Req	2	F2	The unit can run setup for CIP and SIP and product storage operations
UN	55	SY	Req	3	F3	The unit can run vacuum and vacuum hold test.
UN	55	SY	Req	4	F4	The unit can run CIP.
UN	55	SY	Req	5	F5	The unit can run SIP.
UN	55	SY	Req	6	F6	The unit can run receipt of cooled and filtered product from Manufacturing.
UN	55	SY	Req	7	F7	The unit can run transfer to filling.

## tblClass_Transition
Level	ClassID	Class	Transition	Description
CM	15	DI1	T1	Recovery from ALARM state to healthy state when DI signal comes on.
CM	15	DI1	T2	DO signal goes off.
CM	16	DI2	T1	Recovery from ALARM state to healthy state when software signal comes on.
CM	16	DI2	T2	Software signal goes off.
CM	17	HE1	T1	Heating element is switched to OFF
CM	17	HE1	T2	Heating element is switched to ON
CM	18	MI1	T1	Data quality of the analog input signal goes out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ).
CM	18	MI1	T2	Analog input signal becomes healthy between 4-20mA.
CM	19	MOD1	T1	Valve CMND is commanded to OPEN. Intrument air supply to control valve is opened. Control valve opens according to position signal POSN it has received. In auto mode POSN is set by temperature controller TC1.
CM	19	MOD1	T2	Valve CMND is commanded to CLOSE. Intrument air supply to control valve is closed. Control valve closes according to position signal POSN it has received. In auto mode POSN is set by temperature controller TC1.
CM	20	MOT1	T1	Motor is STOPPED when CMND is commanded to START
CM	20	MOT1	T2	Motor is RUNNING when CMND is commanded to STOP
CM	20	MOT1	T3	Motor CMND has been commanded to start, TMR is not expired
CM	20	MOT1	T4	Motor CMND has been commanded to stop, TMR is not expired
CM	20	MOT1	T5	Motor is STOPPED and RUNNG feedback turns on.
CM	20	MOT1	T6	Motor is RUNNING and RUNNG feedback turns off.
CM	20	MOT1	T7	Motor CMND has been commanded to START and TMR expired and RUNNG feedback not ON / OR / Motor CMND has been commanded to STOP and TMR expired and RUNNG feedback still ON / OR / Motor OVLND is on.
CM	20	MOT1	T8	Recovery from FAULT state to STOPPED state
CM	22	PC1	T1	Pressure Control is enabled.
CM	22	PC1	T2	Pressure Control is disabled.
CM	22	PC1	T3	Data quality of the analog input signal goes bad.
CM	22	PC1	T4	Data quality of the analog input signal comes good.
CM	21	PI1	T1	Data quality of the analog input signal goes out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ).
CM	21	PI1	T2	Analog input signal becomes healthy between 4-20mA.
CM	23	POS1	T1	Valve is CLOSED when CMND is commanded to OPEN.
CM	23	POS1	T2	Valve is OPENED when CMND is commanded to CLOSE.
CM	24	POS2	T1	Valve is CLOSED when CMND is commanded to OPEN.
CM	24	POS2	T2	Valve is OPENED when CMND is commanded to CLOSE.
CM	24	POS2	T3	Valve CMND has been commanded to OPEN, travel timer is not expired
CM	24	POS2	T4	Valve CMND has been commanded to CLOSE, travel timer is not expired
CM	24	POS2	T5	Valve is CLOSED and CLSD feedback is off.
CM	24	POS2	T6	Valve is OPENED and CLSD feedback is on.
CM	24	POS2	T7	Valve CMND has been commanded to close. Opened feedback CLSD is off. Travel timer TMR has expired / OR / Valve CMND has been commanded to open. Closed feedback CLSD is on. Travel timer TMR has expired
CM	24	POS2	T8	Recovery from FAULT state to CLOSED state
CM	24	POS2	T9	Recovery from FAULT state to OPENED state
CM	25	POS3	T1	Valve is CLOSED when CMND is commanded to OPEN.
CM	25	POS3	T2	Valve is OPENED when CMND is commanded to CLOSE.
CM	25	POS3	T3	Valve CMND has been commanded to OPEN, travel timer is not expired
CM	25	POS3	T4	Valve CMND has been commanded to CLOSE, travel timer is not expired
CM	25	POS3	T5	Valve is CLOSED and CLSD feedback is off.
CM	25	POS3	T6	Valve is OPENED and CLSD feedback is on.
CM	25	POS3	T7	Valve CMND has been commanded to close. Opened feedback CLSD is off. Travel timer TMR has expired / OR / Valve CMND has been commanded to open. Closed feedback CLSD is on. Travel timer TMR has expired
CM	25	POS3	T8	Recovery from FAULT state to CLOSED state
CM	25	POS3	T9	Recovery from FAULT state to OPENED state
CM	26	POS4	T1	Valve is CLOSED when CMND is commanded to OPEN.
CM	26	POS4	T2	Valve is OPENED when CMND is commanded to CLOSE.
CM	26	POS4	T3	Valve CMND has been commanded to OPEN, travel timer is not expired
CM	26	POS4	T4	Valve CMND has been commanded to CLOSE, travel timer is not expired
CM	26	POS4	T5	Valve is CLOSED and CLSD feedback is off or OPND feedback turns on.
CM	26	POS4	T6	Valve is OPENED and OPND feedback is off or CLSD feedback turns on.
CM	26	POS4	T7	Valve CMND has been commanded to close. Opened feedback OPND is on. Travel timer TMR has expired / OR / Valve CMND has been commanded to open. Closed feedback CLSD is on. Travel timer TMR has expired
CM	26	POS4	T8	Recovery from FAULT state to CLOSED state
CM	26	POS4	T9	Recovery from FAULT state to OPENED state
CM	27	SIC1	T1	Speed controller is disabled when CMND is commanded to ENABLED.
CM	27	SIC1	T2	Speed controller is enabled when CMND is commanded to DISABLED.
CM	27	SIC1	T3	Speed controller is disabled when one of the interlock condition are active.
CM	27	SIC1	T4	Speed controller is on Fault status when all of the interlock conditions are cleared.
CM	27	SIC1	T5	Speed controller is enabled, at least one of the interlock conditions is active, motor command will be immediately set to OFF
CM	27	SIC1	T6	Speed controller is enabled, motor is stopped when motor CMND is set to START or Speed setpoint is set to PID Result.
CM	27	SIC1	T7	Speed controller is enabled, motor is running when motor CMND is set to STOP or Speed setpoint to inverter is set to zero.
CM	28	TC1	T1	Data quality of the analog input signal goes out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ).
CM	28	TC1	T2	Analog input signal becomes healthy between 4-20mA.
CM	29	TI1	T1	Data quality of the analog input signal goes out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ).
CM	29	TI1	T2	Analog input signal becomes healthy between 4-20mA.
CM	30	TI2	T1	Data quality of the analog input signal goes out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ).
CM	30	TI2	T2	Analog input signal becomes healthy between 4-20mA.
CM	31	ZSC1	T1	Manway is manually closed by operator. Or wiring fault is resolved.
CM	31	ZSC1	T2	Manway is manually opened by operator.
CM	32	ZSC2	T1	(REQ_STATE) is IN and the input signal is ON
CM	32	ZSC2	T2	(REQ_STATE) is OUT and the input signal is ON
CM	32	ZSC2	T3	(REQ_STATE) is IN and the input signal is OFF
CM	32	ZSC2	T4	(REQ_STATE) is OUT and the input signal is OFF

## tblClass_Alarm
Level	ClassID	Class	Mnemonic	Condition	Priority	Message
CM	15	DI1	DIA	Digital input alarm	H	@@tag@@ fault
CM	18	MI1	MAH	Mass alarm high	M	Vessel mass @@tag@@ high
CM	18	MI1	MAHH	Mass alarm high high	H	Vessel mass @@tag@@ high high
CM	20	MOT1	FAULT	Motor fault	H	@@tag@@ fault
CM	21	PI1	PAH	Pressure @@tag@@ alarm high	M	Pressure @@tag@@ high
CM	21	PI1	PAHH	Pressure @@tag@@ alarm high high	H	Pressure @@tag@@ high high, charging interlocked
CM	21	PI1	PAL	Pressure @@tag@@ alarm low	M	Pressure @@tag@@ low
CM	21	PI1	PALL	Pressure @@tag@@ alarm low low	H	Pressure @@tag@@ low low
CM	26	POS4	FAULT_C	Valved commanded but position switch feedback not correct	H	Valve @@tag@@ failed to close
CM	26	POS4	FAULT_O	Valved commanded but position switch feedback not correct	H	Valve @@tag@@ failed to open
CM	27	SIC1	FLT	Inverter failure	H	Vessel agitator @@tag@@ motor inverter failure
CM	27	SIC1	SAH	Speed alarm high	M	Vessel agitator @@tag@@ speed high
CM	27	SIC1	SAHH	Speed alarm high high	H	Vessel agitator @@tag@@ speed high high
CM	27	SIC1	SAL	Speed alarm low	M	Vessel agitator @@tag@@ speed low
CM	27	SIC1	SALL	Speed alarm low low	H	Vessel agitator @@tag@@ speed low low
CM	27	SIC1	TAH	Motor overheated	H	Vessel agitator @@tag@@ motor overheated
CM	27	SIC1	THR	Motor overcurrent	H	Vessel agitator @@tag@@ motor over current
CM	29	TI1	TAH	Temperature @@tag@@ alarm high	M	Temperature @@tag@@ high
CM	29	TI1	TAHH	Temperature @@tag@@ alarm high high	H	Temperature @@tag@@ high high, charging interlocked
CM	29	TI1	TAL	Temperature @@tag@@ alarm low	M	Temperature @@tag@@ low
CM	29	TI1	TALL	Temperature @@tag@@ alarm low low	H	Temperature @@tag@@ low low
CM	30	TI2	TAH	Temperature @@tag@@ alarm high	M	Temperature @@tag@@ high
CM	30	TI2	TAHH	Temperature @@tag@@ alarm high high	H	Temperature @@tag@@ high high
CM	30	TI2	TAL	Temperature @@tag@@ alarm low	M	Temperature @@tag@@ low
CM	30	TI2	TALL	Temperature @@tag@@ alarm low low	H	Temperature @@tag@@ low low
CM	31	ZSC1	ZSCA	Manway opened with alarm active	H	Manway cover @@tag@@ opened
EM	34	EMC1	TIMEOUT	Timeout waiting to achieve pressure setpoint	M	Vessel (Mx/Sy) taking excessive time to achieve pressure setpoint
EM	35	EMC2	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	35	EMC2	TIMEOUT	Timeout waiting to achieve mass setpoint	M	Vessel Mx taking excessive time to achieve mass setpoint
EM	36	EMC3	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	41	EMT1	TIMEOUT	Timeout waiting to achieve temperature setpoint	M	Vessel (Mx/Sy) taking excessive time to cool
EM	42	EMV1	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	44	EMX1	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	45	EMX2	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	46	EMX4	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	47	EMX5	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
EM	48	EMX6	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup
UN	#N/A	FPZ	FAULT	EM State does not follow Command time-out	H	Flow path is no longer setup.
UN	#N/A	FPZ	FLOWPATH	Flow path device, keypiece or valve, no longer setup	M	EM state verification could not be completed.
UN	53	MX	FAULT	EM State does not follow Command time-out	M	EM state verification could not be completed.
UN	53	MX	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup.
UN	55	SY	FAULT	EM State does not follow Command time-out	M	EM state verification could not be completed.
UN	55	SY	FLOWPATH	Flow path device, keypiece or valve, no longer setup	H	Flow path is no longer setup.

## tblClass_Parameter
Level	ClassID	ParameterClass	State	Parameter	sfcParameter	ParameterDataType	ParameterType	childParameterAlias	ParameterDescription	UoM	ParameterMin	ParameterMax	ParameterValue
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
DEL	0	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL	DEL
CM	19	MOD1		VALVE_POS	_valve_pos	Real	VAR_INPUT	DEL	Local control valve fixed position setting	%	0	100	0
CM	22	PC1		SETPOINT	_setpoint	Real	VAR_INPUT	DEL	Pressure Setpoint	bar	0.0	2.0	1.0
CM	22	PC1		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual measured pressure value from CM PI1	bar	0.0	2.0	1.0
CM	22	PC1		VALVE	_valve	Int	VAR_INPUT	DEL	Compressed air selection value		1=HPCA	2=LPCA	0
CM	21	PI1		LIMIT_L	_limit_l	Real	VAR_INPUT	DEL	Low pressure alarm limit	bar	0	1.0	0.2
CM	21	PI1		ENABLE_L	_enable_l	Real	VAR_INPUT	DEL	Enable low pressure alarm		0 = DISABLED	1 = ENABLED	1
CM	21	PI1		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual pressure measured value	bar	-1.0	5.0	0.0
CM	21	PI1		INTERLOCK	_interlock	Bool	VAR_OUTPUT	DEL	Interlock active flag if; a) high pressure interlock active, or b) DQ is BAD, or c) High pressure switch active		0 = INACTIVE	1 = ACTIVE	0
CM	27	SIC1		SETPOINT	_setpoint	Real	VAR_INPUT	DEL	Speed setpoint	rpm	0	250	0
CM	27	SIC1		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual motor speed measured value	rpm	0	250	0
CM	27	SIC1		MASS_RUN	_mass_run	Real	VAR_INPUT	DEL	Minimum vessel mass to allow the motor to run	kg	TBA	TBA	1000
CM	27	SIC1		INTERLOCK	_interlock	Bool	VAR_OUTPUT	DEL	Interlock Active Flag (set by any Interlock condition below).		0 = Inactive	1 = Active	0
CM	28	TC1		SETPOINT	_setpoint	Real	VAR_INPUT	DEL	Temperature Setpoint	°C	6	130	0
CM	28	TC1		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual measured temperature value from CM TI1	°C	6	130	0
CM	29	TI1		LIMIT_HH	_limit_hh	Real	VAR_INPUT	DEL	High high temperature interlock (high high temperature alarm limit shall be set to the same value)	°C	0	135	132
CM	29	TI1		LIMIT_H	_limit_h	Real	VAR_INPUT	DEL	High temperature alarm limit	°C	0	135	129
CM	29	TI1		LIMIT_L	_limit_l	Real	VAR_INPUT	DEL	Low temperature alarm limit	°C	0	135	2
CM	29	TI1		LIMIT_LL	_limit_ll	Real	VAR_INPUT	DEL	Low low temperature alarm limit	°C	0	135	0
CM	29	TI1		ENABLE_H	_enable_h	Bool	VAR_INPUT	DEL	Enable high temperature alarm		0 = DISABLED	1 = ENABLED	1
CM	29	TI1		ENABLE_L	_enable_l	Bool	VAR_INPUT	DEL	Enable low temperature alarm		0 = DISABLED	0 = DISABLED	1
CM	29	TI1		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual temperature measured value	°C	0	150	0
CM	29	TI1		INTERLOCK	_interlock	Bool	VAR_OUTPUT	DEL	Interlock active flag if; / a) high temperature interlock active, or / b) DQ is BAD		0 = INACTIVE	1 = ACTIVE	0
CM	31	ZSC1		INTERLOCK	_interlock	Bool	VAR_OUTPUT	DEL	Interlock active flag set ACTIVE if DI = OFF.		0 = INACTIVE	1 = ACTIVE	0
CM	31	ZSC1		CUTOUT	_cutout	Bool	VAR_INPUT	DEL	Flag indicating if alarm is cutout (i.e. disabled)		0 = ALARM ENABLED	1 = ALARM DISABLED	0
CM	32	ZSC2		REQ_STATE	_req_state	Int	VAR_INPUT	DEL	The required state, either IN or OUT, of the flowpath device.		0 = OUT	1 = IN	0
CM	18	MI1		LIMIT_H	_limit_h	Real	VAR_INPUT	DEL	High mass alarm limit	kg	0	1400	1400
CM	18	MI1		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual mass measured value	kg	0	1500	0
CM	18	MI1		INTERLOCK	_interlock	Bool	VAR_OUTPUT	DEL	Interlock active flag if data quality is BAD.		0 = INACTIVE	1 = ACTIVE	0
CM	15	DI1		INTERLOCK	_interlock	Bool	VAR_OUTPUT	DEL	Interlock active flag set ACTIVE if DI = OFF.		0 = INACTIVE	1 = ACTIVE	0
CM	30	TI2		MEASURE	_measure	Real	VAR_OUTPUT	DEL	Actual temperature measured value	°C	0	150	0
CM	17	HE1		CUTOUT	_cutout	Bool	VAR_INPUT	DEL	Flag indicating TI alarm is to be cutout (i.e. disabled) whenever HE is OFF.		0 = ALARM ENABLED	1 = ALARM DISABLED	0
EM	33	EMA1	MIX	SETPOINT	_setpoint	Real	VAR_INPUT	SIC_AGIT	Agitator speed setpoint	rpm	0	240	0
EM	34	EMC1	PRESSURE	SETPOINT	_setpoint	Real	VAR_INPUT	PC_VESSEL	Pressure Control setpoint	bar	-0.05	5	1
EM	34	EMC1	PRESSURE	P_BAND_HI	_p_band_hi	Real	VAR_INPUT	PC_VESSEL	High pressure hysteresis value	bar	0	2	0.1
EM	34	EMC1	PRESSURE	P_BAND_LO	_p_band_lo	Real	VAR_INPUT	PC_VESSEL	Low pressure hysteresis value	bar	0	2	0.1
EM	34	EMC1	PRESSURE	TIMEOUT	_timeout	Int	VAR_INPUT		Time out period for pressure not reached alarm	secs	0	10800	500
EM	34	EMC1	VALVE	VALVE	_valve	Int	VAR_INPUT		Selected valve to be opened			1=HPCA, 2=LPCA, 3=VENT, 4=VACUUM, 5=DRAIN	0
EM	35	EMC2	CHARGE	MEDIUM	_medium	Int	VAR_INPUT		Selected medium to be added			1=WFI, 2=PW, 3=PS(WFI), 4=PS(PW)	0
EM	35	EMC2	CHARGE	MASS	_mass	Real	VAR_INPUT		Mass of Medium to be charged	kg	0	15000	0
EM	35	EMC2	CHARGE	TIMEOUT	_timeout	Int	VAR_INPUT		Timeout period for mass charging	mins	0	59	0
EM	35	EMC2	FLUSH	MEDIUM	_medium	Int	VAR_INPUT		Selected medium to be added			1=WFI, 2=PW, 3=PS(WFI), 4=PS(PW)	0
EM	35	EMC2	FLUSH	TIME_FLUSH	_time_flush	Int	VAR_INPUT		Time to flush for or zero to flush forever	mins			0
EM	36	EMC3		MEDIUM	_medium	Int	VAR_INPUT		Selected medium to be added			1=WFI, 2=PW, 3=PS(WFI), 4=PS(PW)	0
EM	36	EMC3		RUN_TO_TIME	_run_to_time	Bool	VAR_INPUT		Flag indicating if flush to preset time		0 = FALSE	1 = TRUE	0
EM	38	EMG1		FILT_TEMP	_filt_temp	Real	VAR_OUTPUT		PV from filter temperature CM	°C	0	150	PV
EM	38	EMG1		SIP_TEMP	_sip_temp	Real	VAR_OUTPUT		PV from SIP temperature CM	°C	0	150	PV
EM	38	EMG1		CUTIN_TEMP	_cutin_temp	Real	VAR_INPUT		Vessel temperature at which to turn on the filter housing heater	°C	0	150	40
EM	38	EMG1		CUTIN_DB	_cutin_db	Real	VAR_INPUT		Deadband value for cutin temperature hysteresis	°C	0	150	2
EM	38	EMG1		CUTOUT_TIME	_cutout_time	Int	VAR_INPUT		Time to turn off filter housing heater once temperature reduces below cut-in temperature less deadband	hours	0	150	1
EM	39	EMM1		MASS_CURRENT	_mass_current	Real	VAR_OUTPUT		Current settled and more accurate vessel gross mass.	kg	0	15000	PV
EM	39	EMM1		MASS_TARE	_mass_tare	Real	VAR_OUTPUT		Saved Tare mass value	kg	0	15000	0
EM	39	EMM1		MASS_NETT	_mass_nett	Real	VAR_OUTPUT		Calculated Nett mass value = Current mass – Tare mass	kg	0	15000	0
EM	41	EMT1		SETPOINT	_setpoint	Real	VAR_INPUT	TC_HEX	PID setpoint	°C	0	150	Calling
EM	41	EMT1		MEASURE	_measure	Real	VAR_OUTPUT	TI_HEX	PV from transfer line temperature probe	°C	0	150	PV
EM	42	EMV1		ENAB_ALM	_enab_alm	Bool	VAR_INPUT		Enable or disable Manway Alarm		0 = FALSE	1 = TRUE	0
EM	43	EMV2		TIME_OPENED	_time_opened	Time	VAR_INPUT		Required opened time for each sprayball inlet valve in flip-flop mode	secs	0	300	5
EM	45	EMX2		MX	_mx	Int	VAR_INPUT		Manufacturing Vessel.			M1, M2
UN	45	EMX2		FLZ	_flz	Int	VAR_INPUT		Filling Line.			FL1, FL2
EM	46	EMX4		SIP_TEMP	_sip_temp	Real	VAR_OUTPUT		PV from Drain line temperature probe	°C			Calling
EM	46	EMX4		TIME_OPENED	_time_opened	Time	VAR_INPUT		Required time to open the SIP valve in pulse mode	secs	0	300	5
EM	46	EMX4		TIME_CLOSED	_time_closed	Time	VAR_INPUT		Required time to close the SIP valve in pulse mode	secs	0	300	5
EM	47	EMX5		PAUSED	_paused	Bool	VAR_INPUT		Filling is paused if push button activated.		0 = FALSE	1 = TRUE	0
EM	48	EMX6		SY	_sy	Int	VAR_INPUT		Storage Vessel Sy			1=S1, 2=S2, 3=S3, 4=S4	0
UN	53	MX		VESSEL	_vessel	Int	VAR_INPUT		Manufacturing Vessel.			M1, M2
UN	53	MX		BATCHNO	_batchno	Int	VAR_INPUT		Batch or cycle number.			Batch No.: Lym999 / Cycle No.: 999999
UN	53	MX		MASS_THROTTLE	_mass_throttle	Real	VAR_INPUT		Mass nearing the end of Transfer	kg	0	15000	0
UN	54	SMFL		SY	_sy	Int	VAR_INPUT		Storage Vessel.			S1, S2
UN	54	SMFL		BATCHNO	_batchno	Int	VAR_INPUT		Batch or cycle number			Batch No.: Lym999 / Cycle No.: 999999
UN	55	SY		SY	_sy	Int	VAR_INPUT		Storage Vessel.			S1, S2
UN	55	SY		FILL_LINE	_fill_line	Int	VAR_INPUT		Filling Line.			BFS1, BFS2
UN	55	SY		BATCHNO	_batchno	Int	VAR_INPUT		Batch or cycle number			Batch No.: Lym999 / Cycle No.: 999999
UN	#N/A	FPZ		BATCHNO	_batchno	Int	VAR_INPUT		Batch or cycle number			Batch No.: Lym999 / Cycle No.: 999999

## tblParameter_Default
Pcell	Parameter	Default	UoM
PCM1	TagIndex	1
PCM2	TagIndex	10
PCS1	TagIndex	20
PCS2	TagIndex	20
PCM1	MaxMass	15000	kg
PCM2	MaxMass	15000	kg
PCS1	MaxMass	15000	kg
PCS2	MaxMass	15000	kg
PCM1	MaxAgit	250	rpm
PCM2	MaxAgit	250	rpm

## tblClass_Selection
Level	Class	Parameter	Selection	SelectionValue
EM	EMC1	MEDIUM	GAS	HPCA
EM	EMC1	MEDIUM	GAS	LPCA
EM	EMC1	MEDIUM	GAS	VENT
EM	EMC1	MEDIUM	GAS	VACUUM
EM	EMC1	MEDIUM	GAS	DRAIN
EM	EMC2	MEDIUM	LIQUID	WFI
EM	EMC2	MEDIUM	LIQUID	PW
EM	EMC2	MEDIUM	LIQUID	PSWFI
EM	EMC2	MEDIUM	LIQUID	PSPW
EM	EMC3	MEDIUM	LIQUID	WFI
EM	EMC3	MEDIUM	LIQUID	PW
EM	EMC3	MEDIUM	LIQUID	PSWFI
EM	EMC3	MEDIUM	LIQUID	PSPW
EM	EMX2	SY	SY	S1
EM	EMX2	SY	SY	S2
EM	EMX6	SY	SY	S1
EM	EMX6	SY	SY	S2

## tblClass_Child
Level	Class	ClassID	childAliasTag	childAlias	childSFCAlias	childAliasClass	childClassID	childAliasDescription	Shared
CM	DI1	15	DI	DI_DI	_di_di	DI	1	Alarm input	No
CM	HE1	17	DO	HE_DO	_he_do	DO	2	Heating element output	No
CM	MI1	18	PV	MI_PV	_mi_pv	PAI	7	Load cell measured value	No
CM	MOD1	19	MOD	MOD_AO	_mod_ao	AO	4	Valve position in %	No
CM	MOD1	19	DO	MOD_DO	_mod_do	DO	2	Enable air supply command	No
CM	MOT1	20	CMND	MOT_CMND	_mot_cmnd	DO	2	Motor RUN / STOP command	No
CM	MOT1	20	FAULT	MOT_FAULT	_mot_fault	DI	1	General Fault	No
CM	MOT1	20	RUN	MOT_RUN	_mot_run	DI	1	Motor Running / Stopped	No
CM	POS1	23	CMND	POS_CMND	_pos_cmnd	PDO	6	Valve OPEN / CLOSE command	No
CM	POS2	24	CMND	POS_CMND	_pos_cmnd	PDO	6	Valve OPEN / CLOSE command	No
CM	POS2	24	ZSC	POS_ZSC	_pos_zsc	DI	1	Valve CLOSED feedback ZSC switch	No
CM	POS3	25	CMND	POS_CMND	_pos_cmnd	PDO	6	Valve OPEN / CLOSE command	No
CM	POS3	25	ZSO	POS_ZSO	_pos_zso	DI	1	Valve OPENED feedback ZSO switch	No
CM	POS4	26	CMND	POS_CMND	_pos_cmnd	PDO	6	Valve OPEN / CLOSE command	No
CM	POS4	26	ZSC	POS_ZSC	_pos_zsc	DI	1	Valve CLOSED feedback ZSC switch	No
CM	POS4	26	ZSO	POS_ZSO	_pos_zso	DI	1	Valve OPENED feedback ZSO switch	No
CM	SIC1	27	SPM	SIC_AI	_sic_ai	PAI	7	Inverter speed measured value	No
CM	SIC1	27	SPS	SIC_AO	_sic_ao	PAO	8	Inverter speed output	No
CM	SIC1	27	CMND	SIC_CMND	_sic_cmnd	PDO	6	Inverter motor RUN / STOP command	No
CM	SIC1	27	FLT	SIC_FLT	_sic_flt	PDI	5	Inverter failure	No
CM	SIC1	27	TAH	SIC_TAH	_sic_tah	PDI	5	Inverter motor high temperature (PTC101)	No
CM	SIC1	27	THR	SIC_THR	_sic_thr	PDI	5	Thermal release (QM1)	No
CM	TI1	29	PV	TI_PV	_ti_pv	AI	3	Temperature Measured Value	No
CM	TI2	30	PV	TI_PV	_ti_pv	AI	3	Temperature Measured Value	No
CM	ZSC1	31	DI	ZSC_DI	_zsc_di	DI	1	Switch input	No
CM	ZSC2	32	DI	ZSC_DI	_zsc_di	DI	1	Switch input	No
EM	EMA1	33	AGn101	SIC_AGIT	_sic_agit	SIC1	27	Mx Agitator	No
EM	EMC1	34	DVn103	POS_HPCA	_pos_hpca	POS2	24	Vessel HP CA Supply Valve	No
EM	EMC1	34	DVn105	POS_LPCA	_pos_lpca	POS2	24	Vessel LP CA Supply Valve	No
EM	EMC1	34	DVn107	POS_VACUUM	_pos_vacuum	POS2	24	Vessel Vacuum valve	No
EM	EMC1	34	DVn101	POS_VENT	_pos_vent	POS2	24	Vessel Vent Valve	No
EM	EMC1	34	BAVn139	POS_VENTDRAIN	_pos_ventdrain	POS4	26	Vessel Vent line drain valve	No
EM	EMC1	34	PCn103	PC_VESSEL	_pc_vessel	PC1	22	Vessel Pressure Controller	No
EM	EMC1	34	PIn103	PI_VESSEL	_pi_vessel	PI1	21	Vessel Pressure Indictor	No
EM	EMC2	35	ZSCn107	ZSC_FPINLET	_zsc_fpinlet	ZSC2	32	Mx inlet line Flowpath Indicator	No
EM	EMC2	35	ZSCn105	ZSC_FPPW	_zsc_fppw	ZSC2	32	Mx PW Supply Flowpath Indicator	No
EM	EMC2	35	ZSCn103	ZSC_FPWFI	_zsc_fpwfi	ZSC2	32	Mx WFI Supply Flowpath Indicator	No
EM	EMC2	35	DVn115	POS_PSPW	_pos_pspw	POS2	24	Mx PS Supply for PW Loop	No
EM	EMC2	35	DVn109	POS_PSWFI	_pos_pswfi	POS2	24	Mx PS Supply for WFI Loop	No
EM	EMC2	35	DVn113	POS_PW	_pos_pw	POS4	26	Mx PW Supply Valve	No
EM	EMC2	35	DVn111	POS_WFI	_pos_wfi	POS4	26	Mx WFI Supply Valve	No
EM	EMC3	36	ZSCn107	ZSC_FPINLET	_zsc_fpinlet	ZSC2	32	Sy Inlet line Flowpath Indicator	No
EM	EMC3	36	ZSCn105	ZSC_FPPW	_zsc_fppw	ZSC2	32	Sy PW Supply Flowpath Indicator	No
EM	EMC3	36	ZSCn103	ZSC_FPWFI	_zsc_fpwfi	ZSC2	32	Sy WFI Supply Flowpath Indicator	No
EM	EMC3	36	DVn115	POS_PSPW	_pos_pspw	POS2	24	Sy PS Supply for PW Loop	No
EM	EMC3	36	DVn109	POS_PSWFI	_pos_pswfi	POS2	24	Sy PS Supply for WFI Loop	No
EM	EMC3	36	DVn113	POS_PW	_pos_pw	POS4	26	Sy PW Supply Valve	No
EM	EMC3	36	DVn111	POS_WFI	_pos_wfi	POS4	26	Sy WFI Supply Valve	No
EM	EMC5	37	VPn000	MOT_PUMP1	_mot_pump1	MOT1	20	Vacuum Pump 1	No
EM	EMC5	37	VPn001	MOT_PUMP2	_mot_pump2	MOT1	20	Vacuum Pump 2	No
EM	EMG1	38	TIn103	TI_DRAIN	_ti_drain	TI2	30	Mx Vent Filter top outlet temperature	No
EM	EMG1	38	HEn101	HE_FILTER	_he_filter	HE1	17	Mx Electric Heating Element	No
EM	EMG1	38	TIn101	TI_VENT	_ti_vent	TI2	30	Mx Vent Filter Temperature Indicator	No
EM	EMG1	38	BAVn141	POS_VENTDRAIN	_pos_ventdrain	POS4	26	Mx Vent Filter AF1101 Drain valve	No
EM	EMM1	39	MIn101	MI_VESSEL	_mi_vessel	MI1	18	Mx Mass Indicator	No
EM	EMS1	40	ASLn000	DI_ASL	_di_asl	DI1	15	Instrument air pressure low	No
EM	EMS1	40	ESn100	DI_ESTOP	_di_estop	DI1	15	Emergency Stop	No
EM	EMS1	40	ESn101	DI_ESTOPDUP	_di_estopdup	DI1	15	Emergency Stop	No
EM	EMT1	41	TCn109	TC_HEX	_tc_hex	TC1	28	Mx Inline Heat Exchanger Temperature Controller	No
EM	EMT1	41	TIn109	TI_HEX	_ti_hex	TI1	29	Mx Inline Heat Exchanger Temperature Indictor	No
EM	EMT1	41	BVn153	POS_RETURN	_pos_return	POS1	23	Mx Cooling Water Return Valve	No
EM	EMT1	41	BAVn169	POS_RETURNDRAIN	_pos_returndrain	POS4	26	MMFLx Cooling Water Return Drain Valve	No
EM	EMT1	41	BVn151	POS_SUPPLY	_pos_supply	POS1	23	Mx Cooling Water Supply Valve	No
EM	EMT1	41	BAVn167	POS_SUPPLYDRAIN	_pos_supplydrain	POS4	26	MMFLx Cooling Water Supply Drain Valve	No
EM	EMT1	41	TCVn157	MOD_TCV	_mod_tcv	MOD1	19	Mx cooling water supply valve	No
EM	EMV1	42	RDn101	DI_BURST	_di_burst	DI1	15	Vessel Burst Disc	No
EM	EMV1	42	ZSCn101	ZSC_MANWAY	_zsc_manway	ZSC1	31	Vessel Manway Position	No
EM	EMV1	42	DVn121	POS_OUTLET	_pos_outlet	POS2	24	Vessel Outlet Valve	No
EM	EMV1	42	TIn105	TI_VESSEL	_ti_vessel	TI1	29	Vessel Temperature Indicator	No
EM	EMV2	43	DVn117	POS_SPRAYBALL1	_pos_sprayball1	POS2	24	Vessel Spray Ball 1 Valve	No
EM	EMV2	43	DVn119	POS_SPRAYBALL2	_pos_sprayball2	POS2	24	Vessel Spray Ball 2 Valve	No
EM	EMX1	44	ZSCn115	ZSC_CIPSIP	_zsc_cipsip	ZSC2	32	MMFLx Filtration Inlet CIP & SIP Flowpath Indicator	No
EM	EMX1	44	ZSCn113	ZSC_FILTER	_zsc_filter	ZSC2	32	MMFLx Filtration Inlet Flowpath Indicator	No
EM	EMX1	44	DVn171	POS_FILTERINLET	_pos_filterinlet	POS2	24	MMFLx Filtration Line filter inlet drain valve	No
EM	EMX1	44	DVn173	POS_HEXINLET	_pos_hexinlet	POS2	24	MMFLx Inline Heat Exchanger inlet valve	No
EM	EMX2	45	ZSCn115	ZSC_BFS1	_zsc_bfs1	ZSC2	32	Sy to BFS1 P1 Flowpath Indicator	No
EM	EMX2	45	ZSCn117	ZSC_BFS2	_zsc_bfs2	ZSC2	32	Sy to BFS2 P1 Flowpath Indicator	No
EM	EMX2	45	DVn127	POS_DRAIN	_pos_drain	POS2	24	Sy Transfer line valve to drain	No
EM	EMX2	45	DVn129	POS_FILL	_pos_fill	POS2	24	Sy Transfer line valve to filling	No
EM	EMX2	45	DVn125	POS_SMFL	_pos_smfl	POS2	24	Sy Transfer line valve from SMFL	No
EM	EMX2	45	ZSCn111	ZSC_SMFL1	_zsc_smfl1	ZSC2	32	SMFL1 to S1/BFS1 Flowpath Indicator	No
EM	EMX2	45	ZSCn113	ZSC_SMFL2	_zsc_smfl2	ZSC2	32	SMFL2 to S1/BFS1 Flowpath Indicator	No
EM	EMX2	45	DVn123	POS_VESSEL	_pos_vessel	POS2	24	Sy Transfer line valve from vessel	No
EM	EMX4	46	BAVCIP	POS_CIP	_pos_cip	POS4	26	M1 CIP Drain Valve	No
EM	EMX4	46	TISIP	TI_DRAIN	_ti_drain	TI2	30	M1 Drain Temperature Indicator	No
EM	EMX4	46	BAVSIP	POS_SIP	_pos_sip	POS4	26	M1 SIP Condensate Drain Valve	No
EM	EMX5	47	PBn4101	DI_PAUSE	_di_pause	DI2	16	BFSz Pause Push Button	No
EM	EMX6	48	DVn135	POS_DRAIN	_pos_drain	POS2	24	SMFLy Filtration Line filter outlet drain valve	No
EM	EMX6	48	ZSCn111	ZSC_DRAIN	_zsc_drain	ZSC2	32	SMFLy Filtration Outlet CIP Flowpath Indicator	No
EM	EMX6	48	DVn137	POS_FILTER	_pos_filter	POS2	24	SMFLy Filtration Line filter outlet valve	No
EM	EMX6	48	ZSCn109	ZSC_FILTER	_zsc_filter	ZSC2	32	SMFLy Filtration Line outlet T-piece Flowpath Indicator	No
PC	PCSMS	49	Mn	MX_VESSEL	_mx_vessel	MX	53	Manufacturing Vessel	No
PC	PCSMS	49	FLZn	FLZ_FILL	_flz_fill	FLZ	52	BFS 1 Filling Line Fill Pipe	No
SH	PCSMS	49	SMFLn	SMFLX_FILTER	_smflx_filter	SMFL	54	Storage Filtration Line	No
SH	PCSMS	49	VTLn	VTLY_TRANSFER	_vtly_transfer	VTL	56	Vessel Transfer Lines	No
PC	PCSMS	49	Sn	SY_VESSEL	_sy_vessel	SY	55	Storage Vessel	No
UN	FLZ	52	EXn402	EMX_INLET	_emx_inlet	EMX5	47	BFSz Inlet Supply to Filling Machine Line 1	No
UN	MX	53	EXn006	EMX_DRAIN	_emx_drain	EMX4	46	Mx CIP & SIP Drain	No
UN	MX	53	ESn013	EMS_ESTOP	_ems_estop	EMS1	40	Mx Emergency Stop	No
UN	MX	53	EGn005	EMG_FILTER	_emg_filter	EMG1	38	Mx gas filter heating, drain valve and temperature indicator	No
UN	MX	53	ECn001	EMC_GAS	_emc_gas	EMC1	34	Mx LP CA and HP CA supply, Vacuum and Vent	No
UN	MX	53	ETn003	EMT_HEX	_emt_hex	EMT1	41	Manufacturing Filtration Line Heat Exchanger Temperature Control	No
UN	MX	53	EVn008	EMV_INLET	_emv_inlet	EMV2	43	Mx Vessel Inlet Connection	No
UN	MX	53	EXn014	EMX_MFL	_emx_mfl	EMX1	44	Manufacturing Filtration Line	No
UN	MX	53	ECn012	EMC_VACUUM	_emc_vacuum	EMC5	37	Mixing Vessels Vacuum System	No
UN	MX	53	EAn010	EMA_VESSEL	_ema_vessel	EMA1	33	Mx Vessel Agitator	No
UN	MX	53	EMn009	EMM_VESSEL	_emm_vessel	EMM1	39	Mx load cell	No
UN	MX	53	EVn004	EMV_VESSEL	_emv_vessel	EMV1	42	Mx Vessel mounted equipment and valves	No
UN	MX	53	ECn002	EMC_WATER	_emc_water	EMC2	35	Mx WFI and PS supply plus PW and PS supply	No
UN	SMFL	54	EXn011	EMX_DRAIN	_emx_drain	EMX4	46	MFLx CIP & SIP Drain Line	No
UN	SY	55	EXn006	EMX_DRAIN	_emx_drain	EMX4	46	Sy Vessel CIP & SIP Drain	No
UN	SY	55	ESn013	EMS_ESTOP	_ems_estop	EMS1	40	Sy Emergency Stop	No
UN	SY	55	EGn005	EMG_FILTER	_emg_filter	EMG1	38	Sy gas filter heating, drain valve and temperature indicator	No
UN	SY	55	ECn001	EMC_GAS	_emc_gas	EMC1	34	Sy LP CA and HP CA supply, Vacuum and Vent	No
UN	SY	55	EVn008	EMV_INLET	_emv_inlet	EMV2	43	Sy Vessel Inlet Connection	No
UN	SY	55	ECn012	EMC_VACUUM	_emc_vacuum	EMC5	37	Storage Vessels Vacuum System	No
UN	SY	55	EVn004	EMV_VESSEL	_emv_vessel	EMV1	42	Sy vessel mounted equipment and valves	No
UN	SY	55	ECn002	EMC_WATER	_emc_water	EMC3	36	Sy WFI and PS supply plus PW and PS supply	No
SH	SHARE	58	EXn015	EMX_SMFL	_emx_smfl	EMX6	48	Shared EM Mx Filtration Line outlet and Sy CIPSIP path to drain	Yes
SH	SHARE	58	EXn007	EMX_TRANSFER	_emx_transfer	EMX2	45	Shared EM Vessel Transfer Lines	Yes
SI	SITE	57	MPF	MPF	_mpf	PCSMS	49	Site	No
SI	SITE	57	RM	RM	_rm	ROOM	51	Site	No

## tblClass_State
Level	ClassID	Class	State	StateDescription	AlarmState	hasSFC	SFCType	SFC	Key
CM	15	DI1	ALARM	Alarm condition or loop has wiring fault. Signal is OFF.	Yes	FALSE	None	None	DI1_ALARM
CM	15	DI1	ENABLED	Healthy state. Signal is ON.	No	FALSE	None	None	DI1_ENABLED
CM	16	DI2	ALARM	Alarm condition or loop has wiring fault. Software signal is OFF.	Yes	FALSE	None	None	DI2_ALARM
CM	16	DI2	ENABLED	Healthy state. Software signal is ON.	No	FALSE	None	None	DI2_ENABLED
CM	17	HE1	DISABLED	Heating Element is switched off.	No	FALSE	None	None	HE1_DISABLED
CM	17	HE1	ENABLED	Heating Element is switched on	No	FALSE	None	None	HE1_ENABLED
CM	17	HE1	FAULT	Heating Element controller fault digital input indicates fault condition.	Yes	FALSE	None	None	HE1_FAULT
CM	18	MI1	FAULT	AI signal out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ) shall be indicated.	Yes	FALSE	None	None	MI1_FAULT
CM	18	MI1	ENABLED	Healthy state.	No	FALSE	None	None	MI1_ENABLED
CM	19	MOD1	CLOSED	Valve is physically closed.	No	FALSE	None	None	MOD1_CLOSED
CM	19	MOD1	LOCAL	Valve position is set by local setpoint value.	No	FALSE	None	None	MOD1_LOCAL
CM	19	MOD1	REMOTE	Valve position is set by remote value from temperature controller PID output.	No	FALSE	None	None	MOD1_REMOTE
CM	20	MOT1	FAULT	Motor is stopped. RUNNG feedback is on. / Or / Motor is running. RUNNG feedback is off. / Or / Motor General Fault Feedback is On.	Yes	FALSE	None	None	MOT1_FAULT
CM	20	MOT1	RUNNING	Motor is running. RUNNG feedback is on.	No	FALSE	None	None	MOT1_RUNNING
CM	20	MOT1	STARTING / STOPPING	This is a transitory state. / Motor state is moving to STARTING state, TMR not yet expired and RUNNG feedback not ON. / or / Motor state is moving to STOPPING state, TMR not yet expired and RUNNG feedback still ON.	No	FALSE	None	None	MOT1_STARTING / STOPPING
CM	20	MOT1	STOPPED	Motor is stopped. RUNNG feedback is off.	No	FALSE	None	None	MOT1_STOPPED
CM	22	PC1	OFF	Pressure control is turned off.	No	FALSE	None	None	PC1_OFF
CM	22	PC1	ON	Pressure control is turned on and the selected gas inlet valve is opened when the pressure is below the low deadband or closed when the pressure is above the setpoint.	No	FALSE	None	None	PC1_ON
CM	22	PC1	FAULT	AI signal out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ) shall be indicated.	Yes	FALSE	None	None	PC1_FAULT
CM	21	PI1	FAULT	AI signal out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ) shall be indicated.	Yes	FALSE	None	None	PI1_FAULT
CM	21	PI1	ENABLED	Healthy state.	No	FALSE	None	None	PI1_ENABLED
CM	23	POS1	CLOSED	Valve is physically closed.	No	FALSE	None	None	POS1_CLOSED
CM	23	POS1	OPENED	Valve is physically opened.	No	FALSE	None	None	POS1_OPENED
CM	24	POS2	CLOSED	Valve is physically closed, Closed feedback CLSD is on, travel timer TMR has expired	No	FALSE	None	None	POS2_CLOSED
CM	24	POS2	FAULT	Invalid physical state of the valve where: / 1. Valve is open. CLSD feedback is on. / or / 2. Valve is closed. CLSD feedback is off.	Yes	FALSE	None	None	POS2_FAULT
CM	24	POS2	OPENED	Valve is physically open, Closed feedback CLSD is off, travel timer TMR has expired	No	FALSE	None	None	POS2_OPENED
CM	24	POS2	TRAVEL	This is a transitory state. Valve is moving between OPENED and CLOSED states, closed feedback CLSD is off and travel timer has not yet expired.	No	FALSE	None	None	POS2_TRAVEL
CM	25	POS3	CLOSED	Valve is physically closed, OPND feedback is off, travel timer TMR has expired	No	FALSE	None	None	POS3_CLOSED
CM	25	POS3	FAULT	Invalid physical state of the valve where: / 1. Valve is open. OPND feedback is off. / or / 2. Valve is closed. OPND feedback is on.	Yes	FALSE	None	None	POS3_FAULT
CM	25	POS3	OPENED	Valve is physically open, OPND feedback is on, travel timer TMR has expired	No	FALSE	None	None	POS3_OPENED
CM	25	POS3	TRAVEL	This is a transitory state. Valve is moving between OPENED and CLOSED states, opened feedback OPND is off and travel timer has not yet expired.	No	FALSE	None	None	POS3_TRAVEL
CM	26	POS4	CLOSED	Valve is physically closed, OPND feedback is off, Closed feedback CLSD is on, travel timer TMR has expired	No	FALSE	None	None	POS4_CLOSED
CM	26	POS4	FAULT	Invalid physical state of the valve where: / 1. Valve is open. OPND feedback is off. / or / 2. Valve is closed. CLSD feedback is off.	Yes	FALSE	None	None	POS4_FAULT
CM	26	POS4	OPENED	Valve is physically open, OPND feedback is on, Closed feedback CLSD is off, travel timer TMR has expired	No	FALSE	None	None	POS4_OPENED
CM	26	POS4	TRAVEL	This is a transitory state. Valve is moving between OPENED and CLOSED states, opened feedback OPND is off, closed feedback CLSD is off and travel timer has not yet expired.	No	FALSE	None	None	POS4_TRAVEL
CM	27	SIC1	DISABLED	CM is deactivated. Motor is stopped.	No	FALSE	None	None	SIC1_DISABLED
CM	27	SIC1	ENABLED	CM is activated. Motor will run based on mass in vessel. / Refer STOPPED and RUNNING states below.	No	FALSE	None	None	SIC1_ENABLED
CM	27	SIC1	FAULT	At least one of the interlock conditions are active. Motor is stopped.	Yes	FALSE	None	None	SIC1_FAULT
CM	27	SIC1	RUNNING	Vessel mass is above minimum. Motor is running.	No	FALSE	None	None	SIC1_RUNNING
CM	27	SIC1	STOPPED	Vessel mass is low. Motor is stopped.	No	FALSE	None	None	SIC1_STOPPED
CM	29	TI1	FAULT	AI signal out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ) shall be indicated.	Yes	FALSE	None	None	TI1_FAULT
CM	29	TI1	ENABLED	Healthy state.	No	FALSE	None	None	TI1_ENABLED
CM	30	TI2	FAULT	AI signal out of range and does not measure between 4mA (0% of scale) and 20mA (full scale) or if it goes open circuit (such as a broken wire) then bad Data Quality (DQ) shall be indicated.	Yes	FALSE	None	None	TI2_FAULT
CM	30	TI2	ENABLED	Healthy state.	No	FALSE	None	None	TI2_ENABLED
CM	28	TC1	DISABLED	Temperature control is turned off.	No	FALSE	None	None	TC1_DISABLED
CM	28	TC1	ENABLED	Temperature control is turned on with local fixed setpoint value.	No	FALSE	None	None	TC1_ENABLED
CM	31	ZSC1	CLOSED	Signal is on. Manway cover is closed.	No	FALSE	None	None	ZSC1_CLOSED
CM	31	ZSC1	MISMATCH	The required state (REQ_STATE) does not match the actual state.	Yes	FALSE	None	None	ZSC1_MISMATCH
CM	31	ZSC1	OPENED	Signal is off. Manway cover is open. Or wiring fault exists.	Yes	FALSE	None	None	ZSC1_OPENED
CM	32	ZSC2	IN	Input signal is on. Flowpath device is in place	No	FALSE	None	None	ZSC2_IN
CM	32	ZSC2	MISMATCH	The required state (REQ_STATE) does not match the actual state.	Yes	FALSE	None	None	ZSC2_MISMATCH
CM	32	ZSC2	OUT	Input signal is off. Flowpath device is not in place. Or wiring fault exists.	No	FALSE	None	None	ZSC2_OUT
EM	33	EMA1	MIX	Mixing of Manufacturing Vessel	No	TRUE	PH	PH_EMA1_MIX	EMA1_MIX
EM	34	EMC1	PRESSURE	Blanketing and charging air to vessel	No	FALSE	None	None	EMC1_PRESSURE
EM	34	EMC1	VALVE	Opened Selected Valve (Vent, LPCA, HPCA, Vacuum, Drain)	No	FALSE	None	None	EMC1_VALVE
EM	35	EMC2	CHARGE	Preset weight charging to Manufacturing Vessel	No	TRUE	PH	PH_EMC2_CHARGE	EMC2_CHARGE
EM	35	EMC2	FLUSH	Timed Filling of PW/WFI to Manufacturing Vessel	No	TRUE	PH	PH_EMC2_FLUSH	EMC2_FLUSH
EM	35	EMC2	ISOLATE	Disconnect WFI/PW to Manufacturing Vessel	No	TRUE	PH	PH_EMC2_ISOLATE	EMC2_ISOLATE
EM	35	EMC2	SETUP	WFI/PW Setup for Manufacturing Vessel	No	TRUE	PH	PH_EMC2_SETUP	EMC2_SETUP
EM	36	EMC3	FLUSH	Timed Filling of PW/WFI to Storage Vessel	No	TRUE	PH	PH_EMC3_FLUSH	EMC3_FLUSH
EM	36	EMC3	ISOLATE	Disconnect WFI/PW to Storage Vessel	No	TRUE	PH	PH_EMC3_ISOLATE	EMC3_ISOLATE
EM	36	EMC3	SETUP	WFI/PW Setup for Storage Vessel	No	TRUE	PH	PH_EMC3_SETUP	EMC3_SETUP
EM	37	EMC5	VACUUM	Vacuum system is armed and will run if any consumer call for vacuum	No	FALSE	None	None	EMC5_VACUUM
EM	38	EMG1	FILTER	Gas Filtration for Vessel	No	FALSE	None	None	EMG1_FILTER
EM	38	EMG1	SIP	SIP of Gas Filter	No	FALSE	None	None	EMG1_SIP
EM	39	EMM1	MEASURE	Measure the mass of Manufacturing Vessel	No	TRUE	PH	PH_EMM1_MEASURE	EMM1_MEASURE
EM	39	EMM1	TARE	Tare mass measurement of Manufacturing Vessel	No	TRUE	PH	PH_EMM1_TARE	EMM1_TARE
EM	40	EMS1	ENABLED	Emergency stop EM placeholder	No	FALSE	None	None	EMS1_ENABLED
EM	41	EMT1	COOL	Cooling of Product in Heat Exchanger	No	TRUE	PH	PH_EMT1_COOL	EMT1_COOL
EM	41	EMT1	DRAIN	Draining of Heat Exchanger Jacket	No	TRUE	PH	PH_EMT1_DRAIN	EMT1_DRAIN
EM	41	EMT1	PREEMPT	Preemptive cooling of Heat Exchanger	No	TRUE	PH	PH_EMT1_PREEMPT	EMT1_PREEMPT
EM	42	EMV1	DISCHARGE	Tank outlet Discharge	No	FALSE	None	None	EMV1_DISCHARGE
EM	42	EMV1	MANWAY	Vessel Manway Opening	No	TRUE	PH	PH_EMV1_MANWAY	EMV1_MANWAY
EM	42	EMV1	ISOLATE	Vessel Isolated from Environment	No	TRUE	PH	PH_EMV1_ISOLATE	EMV1_ISOLATE
EM	43	EMV2	PULSE	Sprayball inlet valves operate in flip-flop mode	No	TRUE	PH	PH_EMV2_PULSE	EMV2_PULSE
EM	43	EMV2	CHARGE	Charging into Manufacturing Vessel through both sprayballs	No	FALSE	None	None	EMV2_CHARGE
EM	44	EMX1	CIP_MMFLX	CIP_MMFLx Operation for MMFLx	No	FALSE	None	None	EMX1_CIP_MMFLX
EM	44	EMX1	CIP_MX	CIP_Mx Operation for MMFLx	No	FALSE	None	None	EMX1_CIP_MX
EM	44	EMX1	SETUP_CIPSIP	Setup of CIPSIP for MMFLx	No	TRUE	PH	PH_EMX1_SETUP_CIPSIP	EMX1_SETUP_CIPSIP
EM	44	EMX1	SETUP_FILTER	Setup of MMFLx for Filtration Operation	No	TRUE	PH	PH_EMX1_SETUP_FILTER	EMX1_SETUP_FILTER
RM	44	EMX1	FILTER	Filtration Operation of MMFLx	No	FALSE	None	None	EMX1_FILTER
EM	44	EMX1	SIP	SIP Operation for MMFLx	No	FALSE	None	None	EMX1_SIP
EM	45	EMX2	SETUP	Setup flowplate transfer path from source to destination	No	TRUE	PH	PH_EMX2_SETUP	EMX2_SETUP
EM	45	EMX2	ISOLATE	Isolate flowplate transfer path	No	TRUE	PH	PH_EMX2_ISOLATE	EMX2_ISOLATE
EM	45	EMX2	CIP_SY	CIP of Storage Vessel Sy to Sy Drain	No	FALSE	None	None	EMX2_CIP_SY
EM	45	EMX2	FILL_MX	Filling operation from Mixing Vessel Mx direct to Filling Machine FLz	No	FALSE	None	None	EMX2_FILL_MX
EM	45	EMX2	FILL_SY	Filling operation from Storage Vessel Sy to Filling Machine FLz	No	FALSE	None	None	EMX2_FILL_SY
EM	45	EMX2	FILTER	Filling operation from Mixing Vessel Mx to Storage Vessel Sy	No	FALSE	None	None	EMX2_FILTER
EM	45	EMX2	SIP	SIP of Storage Vessel Sy to SMFLx	No	FALSE	None	None	EMX2_SIP
EM	46	EMX4	CIP	CIP Operation for Drain	No	FALSE	None	None	EMX4_CIP
EM	46	EMX4	SIP	SIP Operation for Drain	No	FALSE	None	None	EMX4_SIP
EM	46	EMX4	SIP_PULSE	SIP Pulse Mode Operation for Drain	No	TRUE	PH	PH_EMX4_SIP_PULSE	EMX4_SIP_PULSE
EM	47	EMX5	FILL	Fill Operation	No	FALSE	None	None	EMX5_FILL
EM	48	EMX6	CIP	CIP Operation for SMFLx	No	FALSE	None	None	EMX6_CIP
EM	48	EMX6	SETUP_CIP	Setup of CIPSIP for SMFLx	No	TRUE	PH	PH_EMX6_SETUP_CIP	EMX6_SETUP_CIP
EM	48	EMX6	FILTER	Filtration Operation of SMFLx	No	FALSE	None	None	EMX6_FILTER
EM	48	EMX6	FILTER_BLEED	Filter Bleed Operation of SMFLx	No	FALSE	None	None	EMX6_FILTER_BLEED
EM	48	EMX6	SIP	SIP Operation of SMFLx	No	FALSE	None	None	EMX6_SIP
EM	48	EMX6	SETUP_SIP	Filtration Setup for SMFLx	No	TRUE	PH	PH_EMX6_SETUP_SIP	EMX6_SETUP_SIP
UN	52	FLZ	FILL	CIP, SIP and filling operations from Mx or Sy	No	FALSE	None	None	FLZ_FILL
UN	53	MX	SETUP_CIPSIP	CIPSIP Setup of MMFLx	No	TRUE	UO	UO_MX_SETUP_CIPSIP	MX_SETUP_CIPSIP
UN	53	MX	SETUP_FILTER	Setup of MMFLx for Filtration Operation	No	TRUE	UO	UO_MX_SETUP_FILTER	MX_SETUP_FILTER
UN	53	MX	CIP	Cip of Mx	No	TRUE	UO	UO_MX_CIP	MX_CIP
UN	53	MX	FILTER	Filtration Operation from Mx to Sy	No	TRUE	UO	UO_MX_FILTER	MX_FILTER
UN	53	Mx	FILL_MX	Filling Operation from Mx to FLz	No	TRUE	UO	UO_Mx_FILL_MX	Mx_FILL_MX
UN	53	MX	MAKE	Make Operation of Mx	No	TRUE	UO	UO_MX_MAKE	MX_MAKE
UN	53	MX	SETUP	Setup of Mx	No	TRUE	UO	UO_MX_SETUP	MX_SETUP
UN	53	MX	SIP	Sip of Mx	No	TRUE	UO	UO_MX_SIP	MX_SIP
UN	53	MX	VACUUM	Vacuum of Mx	No	TRUE	UO	UO_MX_VACUUM	MX_VACUUM
UN	54	SMFL	CIP_SETUP	CIP Setup of SMFLx	No	TRUE	UO	UO_SMFL_CIP_SETUP	SMFL_CIP_SETUP
UN	54	SMFL	CIP	CIP Operation of SMFLx	No	TRUE	UO	UO_SMFL_CIP	SMFL_CIP
UN	54	SMFL	FILTER	Filtration Operation of SMFLx	No	TRUE	UO	UO_SMFL_FILTER	SMFL_FILTER
UN	54	SMFL	FILTER_SETUP	Setup of SMFLx for Filtration Operation	No	TRUE	UO	UO_SMFL_FILTER_SETUP	SMFL_FILTER_SETUP
UN	54	SMFL	SIP	SIP Operation of SMFLx	No	TRUE	UO	UO_SMFL_SIP	SMFL_SIP
UN	55	SY	CIP	CIP of Sy	No	TRUE	UO	UO_SY_CIP	SY_CIP
UN	55	SY	FILTER	Filtration from Mx to Sy	No	TRUE	UO	UO_SY_FILTER	SY_FILTER
UN	55	SY	SETUP	Setup of Sy	No	TRUE	UO	UO_SY_SETUP	SY_SETUP
UN	55	SY	SIP	Sip of Sy	No	TRUE	UO	UO_SY_SIP	SY_SIP
UN	55	SY	FILL_SY	Filling Operation from Sy to FLz	No	TRUE	UO	UO_SY_FILL_SY	SY_FILL_SY
UN	55	SY	VACUUM	Vacuum of Sy	No	TRUE	UO	UO_SY_VACUUM	SY_VACUUM
EM	56	VTL	SETUP	Setup flowplate transfer path	No	FALSE	None	None	VTL_SETUP
EM	56	VTL	ISOLATE	Isolate flowplate transfer path	No	FALSE	None	None	VTL_ISOLATE
EM	56	VTL	CIP_SY	Transfer line Setup from Sy to Sy Drain	No	FALSE	None	None	VTL_CIP_SY
EM	56	VTL	FILL_MX	Transfer line Setup from Mx to Filling Machine	No	FALSE	None	None	VTL_FILL_MX
EM	56	VTL	FILL_SY	Transfer line Setup from Sy to Filling Machine	No	FALSE	None	None	VTL_FILL_SY
EM	56	VTL	FILTER	Transfer line Setup from Filter to Sy	No	FALSE	None	None	VTL_FILTER
EM	56	VTL	SIP	Transfer line Setup from Sy to SMFLx	No	FALSE	None	None	VTL_SIP
PC	50	PCSTOR	FILL	Filling to BFS machine	No	TRUE	RP	RP_PCSTOR_FILL	PCSTOR_FILL
PC	50	PCSTOR	CIPSIP	CIPSIP Recipe Procedure	No	TRUE	RP	RP_PCSTOR_CIPSIP	PCSTOR_CIPSIP
PC	50	PCSTOR	FILTER	Mx Filtration to Sy Recipe Procedure	No	TRUE	RP	RP_PCSTOR_FILTER	PCSTOR_FILTER
PC	50	PCSTOR	FILL_MX	Fill from Mx Recipe Procedure	No	TRUE	RP	RP_PCSTOR_FILL_MX	PCSTOR_FILL_MX
PC	50	PCSTOR	FILL_SY	Fill from Sy Recipe Procedure	No	TRUE	RP	RP_PCSTOR_FILL_SY	PCSTOR_FILL_SY
PC	49	PCSMS	CIPSIP	CIPSIP Recipe Procedure	No	TRUE	RP	RP_PCSMS_CIPSIP	PCSMS_CIPSIP
PC	49	PCSMS	MAKE	Manufacturing Recipe Procedure	No	TRUE	RP	RP_PCSMS_MAKE	PCSMS_MAKE

## tblClass_ChildStateValues
Class	State	childAliasTag	childAlias	childClass	childKey	Condition	Selection	SelectionSet	SelctionValue	trueStatement	trueCommand	falseStatement	falseCommand
EMA1	MIX	AGn101	SIC_AGIT	SIC1	EMA1_MIX_AGn101					L "dbCONST".BLK.SIC1.CMD.DISABLE; / T #SIC_AGIT_CMD;	DISABLE	NOP 0;		EMA1_MIX
EMC1	PRESSURE	DVn105	POS_LPCA	POS2	EMC1_PRESSURE_DVn105					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_LPCA_CMD;	CLOSE	NOP 0;		EMC1_PRESSURE
EMC1	PRESSURE	PIn103	PI_VESSEL	PI1	EMC1_PRESSURE_PIn103					L "dbCONST".BLK.PI1.CMD.ENABLE; / T #PI_VESSEL_CMD;	ENABLE	NOP 0;		EMC1_PRESSURE
EMC1	PRESSURE	PCn103	PC_VESSEL	PC1	EMC1_PRESSURE_PCn103					L "dbCONST".BLK.PC1.CMD.ENABLE; / T #PC_VESSEL_CMD;	ENABLE	NOP 0;		EMC1_PRESSURE
EMC1	PRESSURE	DVn107	POS_VACUUM	POS2	EMC1_PRESSURE_DVn107					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VACUUM_CMD;	CLOSE	NOP 0;		EMC1_PRESSURE
EMC1	PRESSURE	BAVn139	POS_VENTDRAIN	POS4	EMC1_PRESSURE_BAVn139					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_VENTDRAIN_CMD;	CLOSE	NOP 0;		EMC1_PRESSURE
EMC1	PRESSURE	DVn103	POS_HPCA	POS2	EMC1_PRESSURE_DVn103					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_HPCA_CMD;	CLOSE	NOP 0;		EMC1_PRESSURE
EMC1	PRESSURE	DVn101	POS_VENT	POS2	EMC1_PRESSURE_DVn101					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VENT_CMD;	CLOSE	NOP 0;		EMC1_PRESSURE
EMC1	VALVE	BAVn139	POS_VENTDRAIN	POS4	EMC1_VALVE_BAVn139	VALVE = DRAIN	VALVE	GAS	DRAIN	A(; / L #VALVE; / L "dbCONST".SEL.GAS.DRAIN; / ==I; / ); / L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_VENTDRAIN_CMD;	OPEN	A(; / L #VALVE; / L "dbCONST".SEL.GAS.DRAIN; / <>I; / ); / L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_VENTDRAIN_CMD;	CLOSE	EMC1_VALVE
EMC1	VALVE	DVn103	POS_HPCA	POS2	EMC1_VALVE_DVn103	VALVE = HPCA	VALVE	GAS	HPCA	A(; / L #VALVE; / L "dbCONST".SEL.GAS.HPCA; / ==I; / ); / L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_HPCA_CMD;	OPEN	A(; / L #VALVE; / L "dbCONST".SEL.GAS.HPCA; / <>I; / ); / L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_HPCA_CMD;	CLOSE	EMC1_VALVE
EMC1	VALVE	DVn105	POS_LPCA	POS2	EMC1_VALVE_DVn105	VALVE = LPCA	VALVE	GAS	LPCA	A(; / L #VALVE; / L "dbCONST".SEL.GAS.LPCA; / ==I; / ); / L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_LPCA_CMD;	OPEN	A(; / L #VALVE; / L "dbCONST".SEL.GAS.LPCA; / <>I; / ); / L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_LPCA_CMD;	CLOSE	EMC1_VALVE
EMC1	VALVE	DVn107	POS_VACUUM	POS2	EMC1_VALVE_DVn107	VALVE = VACUUM	VALVE	GAS	VACUUM	A(; / L #VALVE; / L "dbCONST".SEL.GAS.VACUUM; / ==I; / ); / L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_VACUUM_CMD;	OPEN	A(; / L #VALVE; / L "dbCONST".SEL.GAS.VACUUM; / <>I; / ); / L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VACUUM_CMD;	CLOSE	EMC1_VALVE
EMC1	VALVE	PIn103	PI_VESSEL	PI1	EMC1_VALVE_PIn103					L "dbCONST".BLK.PI1.CMD.ENABLE; / T #PI_VESSEL_CMD;	ENABLE	NOP 0;		EMC1_VALVE
EMC1	VALVE	PCn103	PC_VESSEL	PC1	EMC1_VALVE_PCn103					L "dbCONST".BLK.PC1.CMD.DISABLE; / T #PC_VESSEL_CMD;	DISABLE	NOP 0;		EMC1_VALVE
EMC1	VALVE	DVn101	POS_VENT	POS2	EMC1_VALVE_DVn101	VALVE = VENT	VALVE	GAS	VENT	A(; / L #VALVE; / L "dbCONST".SEL.GAS.VENT; / ==I; / ); / L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_VENT_CMD;	OPEN	A(; / L #VALVE; / L "dbCONST".SEL.GAS.VENT; / <>I; / ); / L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VENT_CMD;	CLOSE	EMC1_VALVE
EMC2	CHARGE	ZSCn105	ZSC_FPPW	ZSC2	EMC2_CHARGE_ZSCn105	MEDIUM = PW	MEDIUM	LIQUID	PW	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPPW_CMD;	IN	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	EMC2_CHARGE
EMC2	CHARGE	DVn115	POS_PSPW	POS2	EMC2_CHARGE_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC2_CHARGE
EMC2	CHARGE	DVn111	POS_WFI	POS4	EMC2_CHARGE_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC2_CHARGE
EMC2	CHARGE	DVn113	POS_PW	POS4	EMC2_CHARGE_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC2_CHARGE
EMC2	CHARGE	ZSCn103	ZSC_FPWFI	ZSC2	EMC2_CHARGE_ZSCn103	MEDIUM = WFI	MEDIUM	LIQUID	WFI	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPWFI_CMD;	IN	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	EMC2_CHARGE
EMC2	CHARGE	DVn109	POS_PSWFI	POS2	EMC2_CHARGE_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC2_CHARGE
EMC2	CHARGE	ZSCn107	ZSC_FPINLET	ZSC2	EMC2_CHARGE_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPINLET_CMD;	IN	NOP 0;		EMC2_CHARGE
EMC2	FLUSH	ZSCn105	ZSC_FPPW	ZSC2	EMC2_FLUSH_ZSCn105	(MEDIUM = PW OR / MEDIUM = PS(PW))	MEDIUM	LIQUID	PW OR PS(PW)	A(; / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSPW; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPPW_CMD;	IN	A(; / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSPW; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	EMC2_FLUSH
EMC2	FLUSH	DVn113	POS_PW	POS4	EMC2_FLUSH_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC2_FLUSH
EMC2	FLUSH	DVn115	POS_PSPW	POS2	EMC2_FLUSH_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC2_FLUSH
EMC2	FLUSH	ZSCn103	ZSC_FPWFI	ZSC2	EMC2_FLUSH_ZSCn103	(MEDIUM = WFI OR / MEDIUM = PS(WFI))	MEDIUM	LIQUID	WFI OR PS(WFI)	A(; / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSWFI; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPWFI_CMD;	IN	A(; / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSWFI; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	EMC2_FLUSH
EMC2	FLUSH	ZSCn107	ZSC_FPINLET	ZSC2	EMC2_FLUSH_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPINLET_CMD;	IN	NOP 0;		EMC2_FLUSH
EMC2	FLUSH	DVn111	POS_WFI	POS4	EMC2_FLUSH_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC2_FLUSH
EMC2	FLUSH	DVn109	POS_PSWFI	POS2	EMC2_FLUSH_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC2_FLUSH
EMC2	ISOLATE	DVn113	POS_PW	POS4	EMC2_ISOLATE_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC2_ISOLATE
EMC2	ISOLATE	DVn111	POS_WFI	POS4	EMC2_ISOLATE_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC2_ISOLATE
EMC2	ISOLATE	ZSCn103	ZSC_FPWFI	ZSC2	EMC2_ISOLATE_ZSCn103					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	NOP 0;		EMC2_ISOLATE
EMC2	ISOLATE	ZSCn107	ZSC_FPINLET	ZSC2	EMC2_ISOLATE_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPINLET_CMD;	OUT	NOP 0;		EMC2_ISOLATE
EMC2	ISOLATE	DVn115	POS_PSPW	POS2	EMC2_ISOLATE_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC2_ISOLATE
EMC2	ISOLATE	ZSCn105	ZSC_FPPW	ZSC2	EMC2_ISOLATE_ZSCn105					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	NOP 0;		EMC2_ISOLATE
EMC2	ISOLATE	DVn109	POS_PSWFI	POS2	EMC2_ISOLATE_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC2_ISOLATE
EMC2	SETUP	ZSCn107	ZSC_FPINLET	ZSC2	EMC2_SETUP_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPINLET_CMD;	IN	NOP 0;		EMC2_SETUP
EMC2	SETUP	DVn109	POS_PSWFI	POS2	EMC2_SETUP_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC2_SETUP
EMC2	SETUP	DVn115	POS_PSPW	POS2	EMC2_SETUP_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC2_SETUP
EMC2	SETUP	DVn113	POS_PW	POS4	EMC2_SETUP_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC2_SETUP
EMC2	SETUP	ZSCn103	ZSC_FPWFI	ZSC2	EMC2_SETUP_ZSCn103	(MEDIUM = WFI OR / MEDIUM = PS(WFI))	MEDIUM	LIQUID	WFI OR PS(WFI)	A(; / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSWFI; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPWFI_CMD;	IN	A(; / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSWFI; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	EMC2_SETUP
EMC2	SETUP	DVn111	POS_WFI	POS4	EMC2_SETUP_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC2_SETUP
EMC2	SETUP	ZSCn105	ZSC_FPPW	ZSC2	EMC2_SETUP_ZSCn105	(MEDIUM = PW OR / MEDIUM = PS(PW))	MEDIUM	LIQUID	PW OR PS(PW)	A(; / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSPW; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPPW_CMD;	IN	A(; / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSPW; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	EMC2_SETUP
EMC3	FLUSH	ZSCn105	ZSC_FPPW	ZSC2	EMC3_FLUSH_ZSCn105	(MEDIUM = PW OR / MEDIUM = PS(PW))	MEDIUM	LIQUID	PW OR PS(PW)	A(; / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSPW; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPPW_CMD;	IN	A(; / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSPW; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	EMC3_FLUSH
EMC3	FLUSH	DVn115	POS_PSPW	POS2	EMC3_FLUSH_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC3_FLUSH
EMC3	FLUSH	DVn109	POS_PSWFI	POS2	EMC3_FLUSH_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC3_FLUSH
EMC3	FLUSH	DVn113	POS_PW	POS4	EMC3_FLUSH_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC3_FLUSH
EMC3	FLUSH	DVn111	POS_WFI	POS4	EMC3_FLUSH_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC3_FLUSH
EMC3	FLUSH	ZSCn107	ZSC_FPINLET	ZSC2	EMC3_FLUSH_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPINLET_CMD;	IN	NOP 0;		EMC3_FLUSH
EMC3	FLUSH	ZSCn103	ZSC_FPWFI	ZSC2	EMC3_FLUSH_ZSCn103	(MEDIUM = WFI OR / MEDIUM = PS(WFI))	MEDIUM	LIQUID	WFI OR PS(WFI)	A(; / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / O(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSWFI; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPWFI_CMD;	IN	A(; / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / AN(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PSWFI; / ==I; / ); / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	EMC3_FLUSH
EMC3	ISOLATE	ZSCn103	ZSC_FPWFI	ZSC2	EMC3_ISOLATE_ZSCn103					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	NOP 0;		EMC3_ISOLATE
EMC3	ISOLATE	DVn113	POS_PW	POS4	EMC3_ISOLATE_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC3_ISOLATE
EMC3	ISOLATE	DVn111	POS_WFI	POS4	EMC3_ISOLATE_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC3_ISOLATE
EMC3	ISOLATE	ZSCn107	ZSC_FPINLET	ZSC2	EMC3_ISOLATE_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPINLET_CMD;	OUT	NOP 0;		EMC3_ISOLATE
EMC3	ISOLATE	DVn115	POS_PSPW	POS2	EMC3_ISOLATE_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC3_ISOLATE
EMC3	ISOLATE	DVn109	POS_PSWFI	POS2	EMC3_ISOLATE_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC3_ISOLATE
EMC3	ISOLATE	ZSCn105	ZSC_FPPW	ZSC2	EMC3_ISOLATE_ZSCn105					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	NOP 0;		EMC3_ISOLATE
EMC3	SETUP	ZSCn107	ZSC_FPINLET	ZSC2	EMC3_SETUP_ZSCn107					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPINLET_CMD;	IN	NOP 0;		EMC3_SETUP
EMC3	SETUP	ZSCn105	ZSC_FPPW	ZSC2	EMC3_SETUP_ZSCn105	MEDIUM = PW	MEDIUM	LIQUID	PW	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPPW_CMD;	IN	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.PW; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPPW_CMD;	OUT	EMC3_SETUP
EMC3	SETUP	DVn113	POS_PW	POS4	EMC3_SETUP_DVn113					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_PW_CMD;	CLOSE	NOP 0;		EMC3_SETUP
EMC3	SETUP	ZSCn103	ZSC_FPWFI	ZSC2	EMC3_SETUP_ZSCn103	MEDIUM = WFI	MEDIUM	LIQUID	WFI	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FPWFI_CMD;	IN	A(; / L #MEDIUM; / L "dbCONST".SEL.LIQUID.WFI; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FPWFI_CMD;	OUT	EMC3_SETUP
EMC3	SETUP	DVn115	POS_PSPW	POS2	EMC3_SETUP_DVn115					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSPW_CMD;	CLOSE	NOP 0;		EMC3_SETUP
EMC3	SETUP	DVn111	POS_WFI	POS4	EMC3_SETUP_DVn111					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_WFI_CMD;	CLOSE	NOP 0;		EMC3_SETUP
EMC3	SETUP	DVn109	POS_PSWFI	POS2	EMC3_SETUP_DVn109					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_PSWFI_CMD;	CLOSE	NOP 0;		EMC3_SETUP
EMC5	VACUUM	VPn000	MOT_PUMP1	MOT1	EMC5_VACUUM_VPn000					L "dbCONST".BLK.MOT1.CMD.STOP; / T #MOT_PUMP1_CMD;	STOP	NOP 0;		EMC5_VACUUM
EMC5	VACUUM	VPn001	MOT_PUMP2	MOT1	EMC5_VACUUM_VPn001					L "dbCONST".BLK.MOT1.CMD.STOP; / T #MOT_PUMP2_CMD;	STOP	NOP 0;		EMC5_VACUUM
EMG1	FILTER	BAVn141	POS_VENTDRAIN	POS4	EMG1_FILTER_BAVn141					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_VENTDRAIN_CMD;	CLOSE	NOP 0;		EMG1_FILTER
EMG1	FILTER	TIn103	TI_DRAIN	TI2	EMG1_FILTER_TIn103					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_DRAIN_CMD;	ENABLE	NOP 0;		EMG1_FILTER
EMG1	FILTER	HEn101	HE_FILTER	HE1	EMG1_FILTER_HEn101					L "dbCONST".BLK.HE1.CMD.ON; / T #HE_FILTER_CMD;	ON	NOP 0;		EMG1_FILTER
EMG1	FILTER	TIn101	TI_VENT	TI2	EMG1_FILTER_TIn101					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_VENT_CMD;	ENABLE	NOP 0;		EMG1_FILTER
EMG1	SIP	BAVn141	POS_VENTDRAIN	POS4	EMG1_SIP_BAVn141					L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_VENTDRAIN_CMD;	OPEN	NOP 0;		EMG1_SIP
EMG1	SIP	TIn103	TI_DRAIN	TI2	EMG1_SIP_TIn103					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_DRAIN_CMD;	ENABLE	NOP 0;		EMG1_SIP
EMG1	SIP	TIn101	TI_VENT	TI2	EMG1_SIP_TIn101					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_VENT_CMD;	ENABLE	NOP 0;		EMG1_SIP
EMG1	SIP	HEn101	HE_FILTER	HE1	EMG1_SIP_HEn101					L "dbCONST".BLK.HE1.CMD.ON; / T #HE_FILTER_CMD;	ON	NOP 0;		EMG1_SIP
EMM1	MEASURE	MIn101	MI_VESSEL	MI1	EMM1_MEASURE_MIn101					L "dbCONST".BLK.MI1.CMD.ENABLE; / T #MI_VESSEL_CMD;	ENABLE	NOP 0;		EMM1_MEASURE
EMM1	TARE	MIn101	MI_VESSEL	MI1	EMM1_TARE_MIn101					L "dbCONST".BLK.MI1.CMD.ENABLE; / T #MI_VESSEL_CMD;	ENABLE	NOP 0;		EMM1_TARE
EMT1	COOL	BAVn167	POS_SUPPLYDRAIN	POS4	EMT1_COOL_BAVn167					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_SUPPLYDRAIN_CMD;	CLOSE	NOP 0;		EMT1_COOL
EMT1	COOL	TIn109	TI_HEX	TI1	EMT1_COOL_TIn109					L "dbCONST".BLK.TI1.CMD.ENABLE; / T #TI_HEX_CMD;	ENABLE	NOP 0;		EMT1_COOL
EMT1	COOL	TCn109	TC_HEX	TC1	EMT1_COOL_TCn109					L "dbCONST".BLK.TC1.CMD.ENABLE; / T #TC_HEX_CMD;	ENABLE	NOP 0;		EMT1_COOL
EMT1	COOL	BVn153	POS_RETURN	POS1	EMT1_COOL_BVn153					L "dbCONST".BLK.POS1.CMD.OPEN; / T #POS_RETURN_CMD;	OPEN	NOP 0;		EMT1_COOL
EMT1	COOL	TCVn157	MOD_TCV	MOD1	EMT1_COOL_TCVn157					L "dbCONST".BLK.MOD1.CMD.REMOTE; / T #MOD_TCV_CMD;	REMOTE	NOP 0;		EMT1_COOL
EMT1	COOL	BAVn169	POS_RETURNDRAIN	POS4	EMT1_COOL_BAVn169					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_RETURNDRAIN_CMD;	CLOSE	NOP 0;		EMT1_COOL
EMT1	COOL	BVn151	POS_SUPPLY	POS1	EMT1_COOL_BVn151					L "dbCONST".BLK.POS1.CMD.OPEN; / T #POS_SUPPLY_CMD;	OPEN	NOP 0;		EMT1_COOL
EMT1	DRAIN	BVn151	POS_SUPPLY	POS1	EMT1_DRAIN_BVn151					L "dbCONST".BLK.POS1.CMD.CLOSE; / T #POS_SUPPLY_CMD;	CLOSE	NOP 0;		EMT1_DRAIN
EMT1	DRAIN	BVn153	POS_RETURN	POS1	EMT1_DRAIN_BVn153					L "dbCONST".BLK.POS1.CMD.CLOSE; / T #POS_RETURN_CMD;	CLOSE	NOP 0;		EMT1_DRAIN
EMT1	DRAIN	BAVn167	POS_SUPPLYDRAIN	POS4	EMT1_DRAIN_BAVn167					L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_SUPPLYDRAIN_CMD;	OPEN	NOP 0;		EMT1_DRAIN
EMT1	DRAIN	TCVn157	MOD_TCV	MOD1	EMT1_DRAIN_TCVn157					L "dbCONST".BLK.MOD1.CMD.CLOSE; / T #MOD_TCV_CMD;	CLOSE	NOP 0;		EMT1_DRAIN
EMT1	DRAIN	TIn109	TI_HEX	TI1	EMT1_DRAIN_TIn109					L "dbCONST".BLK.TI1.CMD.ENABLE; / T #TI_HEX_CMD;	ENABLE	NOP 0;		EMT1_DRAIN
EMT1	DRAIN	TCn109	TC_HEX	TC1	EMT1_DRAIN_TCn109					L "dbCONST".BLK.TC1.CMD.DISABLE; / T #TC_HEX_CMD;	DISABLE	NOP 0;		EMT1_DRAIN
EMT1	DRAIN	BAVn169	POS_RETURNDRAIN	POS4	EMT1_DRAIN_BAVn169					L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_RETURNDRAIN_CMD;	OPEN	NOP 0;		EMT1_DRAIN
EMT1	PREEMPT	BVn153	POS_RETURN	POS1	EMT1_PREEMPT_BVn153					L "dbCONST".BLK.POS1.CMD.OPEN; / T #POS_RETURN_CMD;	OPEN	NOP 0;		EMT1_PREEMPT
EMT1	PREEMPT	BAVn167	POS_SUPPLYDRAIN	POS4	EMT1_PREEMPT_BAVn167					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_SUPPLYDRAIN_CMD;	CLOSE	NOP 0;		EMT1_PREEMPT
EMT1	PREEMPT	BVn151	POS_SUPPLY	POS1	EMT1_PREEMPT_BVn151					L "dbCONST".BLK.POS1.CMD.OPEN; / T #POS_SUPPLY_CMD;	OPEN	NOP 0;		EMT1_PREEMPT
EMT1	PREEMPT	BAVn169	POS_RETURNDRAIN	POS4	EMT1_PREEMPT_BAVn169					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_RETURNDRAIN_CMD;	CLOSE	NOP 0;		EMT1_PREEMPT
EMT1	PREEMPT	TIn109	TI_HEX	TI1	EMT1_PREEMPT_TIn109					L "dbCONST".BLK.TI1.CMD.ENABLE; / T #TI_HEX_CMD;	ENABLE	NOP 0;		EMT1_PREEMPT
EMT1	PREEMPT	TCn109	TC_HEX	TC1	EMT1_PREEMPT_TCn109					L "dbCONST".BLK.TC1.CMD.DISABLE; / T #TC_HEX_CMD;	DISABLE	NOP 0;		EMT1_PREEMPT
EMT1	PREEMPT	TCVn157	MOD_TCV	MOD1	EMT1_PREEMPT_TCVn157					L "dbCONST".BLK.MOD1.CMD.LOCAL; / T #MOD_TCV_CMD;	LOCAL	NOP 0;		EMT1_PREEMPT
EMV1	DISCHARGE	ZSCn101	ZSC_MANWAY	ZSC1	EMV1_DISCHARGE_ZSCn101					L "dbCONST".BLK.ZSC1.CMD.CLOSE; / T #ZSC_MANWAY_CMD;	CLOSE	NOP 0;		EMV1_DISCHARGE
EMV1	DISCHARGE	TIn105	TI_VESSEL	TI1	EMV1_DISCHARGE_TIn105					L "dbCONST".BLK.TI1.CMD.ENABLE; / T #TI_VESSEL_CMD;	ENABLE	NOP 0;		EMV1_DISCHARGE
EMV1	DISCHARGE	RDn101	DI_BURST	DI1	EMV1_DISCHARGE_RDn101					L "dbCONST".BLK.DI1.CMD.ENABLE; / T #DI_BURST_CMD;	ENABLE	NOP 0;		EMV1_DISCHARGE
EMV1	DISCHARGE	DVn121	POS_OUTLET	POS2	EMV1_DISCHARGE_DVn121					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_OUTLET_CMD;	OPEN	NOP 0;		EMV1_DISCHARGE
EMV1	MANWAY	DVn121	POS_OUTLET	POS2	EMV1_MANWAY_DVn121					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_OUTLET_CMD;	CLOSE	NOP 0;		EMV1_MANWAY
EMV1	MANWAY	ZSCn101	ZSC_MANWAY	ZSC1	EMV1_MANWAY_ZSCn101					L "dbCONST".BLK.ZSC1.CMD.OPEN; / T #ZSC_MANWAY_CMD;	OPEN	NOP 0;		EMV1_MANWAY
EMV1	MANWAY	TIn105	TI_VESSEL	TI1	EMV1_MANWAY_TIn105					L "dbCONST".BLK.TI1.CMD.ENABLE; / T #TI_VESSEL_CMD;	ENABLE	NOP 0;		EMV1_MANWAY
EMV1	MANWAY	RDn101	DI_BURST	DI1	EMV1_MANWAY_RDn101					L "dbCONST".BLK.DI1.CMD.ENABLE; / T #DI_BURST_CMD;	ENABLE	NOP 0;		EMV1_MANWAY
EMV2	PULSE	DVn117	POS_SPRAYBALL1	POS2	EMV2_PULSE_DVn117					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_SPRAYBALL1_CMD;	CLOSE	NOP 0;		EMV2_PULSE
EMV2	PULSE	DVn119	POS_SPRAYBALL2	POS2	EMV2_PULSE_DVn119					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_SPRAYBALL2_CMD;	CLOSE	NOP 0;		EMV2_PULSE
EMV2	CHARGE	DVn117	POS_SPRAYBALL1	POS2	EMV2_CHARGE_DVn117					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_SPRAYBALL1_CMD;	OPEN	NOP 0;		EMV2_CHARGE
EMV2	CHARGE	DVn119	POS_SPRAYBALL2	POS2	EMV2_CHARGE_DVn119					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_SPRAYBALL2_CMD;	OPEN	NOP 0;		EMV2_CHARGE
EMX1	CIP_MMFLX	ZSCn115	ZSC_CIPSIP	ZSC2	EMX1_CIP_MMFLX_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	NOP 0;		EMX1_CIP_MMFLX
EMX1	CIP_MMFLX	DVn173	POS_HEXINLET	POS2	EMX1_CIP_MMFLX_DVn173					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_HEXINLET_CMD;	OPEN	NOP 0;		EMX1_CIP_MMFLX
EMX1	CIP_MMFLX	ZSCn113	ZSC_FILTER	ZSC2	EMX1_CIP_MMFLX_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	NOP 0;		EMX1_CIP_MMFLX
EMX1	CIP_MMFLX	DVn171	POS_FILTERINLET	POS2	EMX1_CIP_MMFLX_DVn171					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTERINLET_CMD;	CLOSE	NOP 0;		EMX1_CIP_MMFLX
EMX1	CIP_MX	ZSCn115	ZSC_CIPSIP	ZSC2	EMX1_CIP_MX_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	NOP 0;		EMX1_CIP_MX
EMX1	CIP_MX	DVn171	POS_FILTERINLET	POS2	EMX1_CIP_MX_DVn171					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILTERINLET_CMD;	OPEN	NOP 0;		EMX1_CIP_MX
EMX1	CIP_MX	ZSCn113	ZSC_FILTER	ZSC2	EMX1_CIP_MX_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	NOP 0;		EMX1_CIP_MX
EMX1	CIP_MX	DVn173	POS_HEXINLET	POS2	EMX1_CIP_MX_DVn173					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_HEXINLET_CMD;	CLOSE	NOP 0;		EMX1_CIP_MX
EMX1	CIPSIP_SETUP	DVn173	POS_HEXINLET	POS2	EMX1_CIPSIP_SETUP_DVn173					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_HEXINLET_CMD;	CLOSE	NOP 0;		#N/A
EMX1	CIPSIP_SETUP	ZSCn115	ZSC_CIPSIP	ZSC2	EMX1_CIPSIP_SETUP_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	NOP 0;		#N/A
EMX1	CIPSIP_SETUP	DVn171	POS_FILTERINLET	POS2	EMX1_CIPSIP_SETUP_DVn171					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTERINLET_CMD;	CLOSE	NOP 0;		#N/A
EMX1	CIPSIP_SETUP	ZSCn113	ZSC_FILTER	ZSC2	EMX1_CIPSIP_SETUP_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	NOP 0;		#N/A
EMX1	FILTER	DVn173	POS_HEXINLET	POS2	EMX1_FILTER_DVn173					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_HEXINLET_CMD;	OPEN	NOP 0;		EMX1_FILTER
EMX1	FILTER	DVn171	POS_FILTERINLET	POS2	EMX1_FILTER_DVn171					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTERINLET_CMD;	CLOSE	NOP 0;		EMX1_FILTER
EMX1	FILTER	ZSCn113	ZSC_FILTER	ZSC2	EMX1_FILTER_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	NOP 0;		EMX1_FILTER
EMX1	FILTER	ZSCn115	ZSC_CIPSIP	ZSC2	EMX1_FILTER_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	NOP 0;		EMX1_FILTER
EMX1	FILTER_SETUP	DVn173	POS_HEXINLET	POS2	EMX1_FILTER_SETUP_DVn173					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_HEXINLET_CMD;	CLOSE	NOP 0;		#N/A
EMX1	FILTER_SETUP	DVn171	POS_FILTERINLET	POS2	EMX1_FILTER_SETUP_DVn171					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTERINLET_CMD;	CLOSE	NOP 0;		#N/A
EMX1	FILTER_SETUP	ZSCn115	ZSC_CIPSIP	ZSC2	EMX1_FILTER_SETUP_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	NOP 0;		#N/A
EMX1	FILTER_SETUP	ZSCn113	ZSC_FILTER	ZSC2	EMX1_FILTER_SETUP_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	NOP 0;		#N/A
EMX1	SIP	ZSCn113	ZSC_FILTER	ZSC2	EMX1_SIP_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	NOP 0;		EMX1_SIP
EMX1	SIP	ZSCn115	ZSC_CIPSIP	ZSC2	EMX1_SIP_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	NOP 0;		EMX1_SIP
EMX1	SIP	DVn173	POS_HEXINLET	POS2	EMX1_SIP_DVn173					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_HEXINLET_CMD;	OPEN	NOP 0;		EMX1_SIP
EMX1	SIP	DVn171	POS_FILTERINLET	POS2	EMX1_SIP_DVn171					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILTERINLET_CMD;	OPEN	NOP 0;		EMX1_SIP
EMX2	CIP_SY	DVn123	POS_VESSEL	POS2	EMX2_CIP_SY_DVn123					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_VESSEL_CMD;	OPEN	NOP 0;		EMX2_CIP_SY
EMX2	CIP_SY	DVn125	POS_SMFL	POS2	EMX2_CIP_SY_DVn125					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_SMFL_CMD;	CLOSE	NOP 0;		EMX2_CIP_SY
EMX2	CIP_SY	DVn127	POS_DRAIN	POS2	EMX2_CIP_SY_DVn127					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_DRAIN_CMD;	OPEN	NOP 0;		EMX2_CIP_SY
EMX2	CIP_SY	DVn129	POS_FILL	POS2	EMX2_CIP_SY_DVn129					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILL_CMD;	CLOSE	NOP 0;		EMX2_CIP_SY
EMX2	CIP_SY	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_CIP_SY_ZSCn111	MX = M1		MX	M1	A(; / L #; / L "dbCONST".SEL.MX.M1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT	EMX2_CIP_SY
EMX2	CIP_SY	ZSCn113	ZSC_FILTER	ZSC2	EMX2_CIP_SY_ZSCn113	MX = M2		MX	M2	A(; / L #; / L "dbCONST".SEL.MX.M2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	EMX2_CIP_SY
EMX2	CIP_SY	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_CIP_SY_ZSCn115	FLZ=FL1		FLZ	FL1	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	EMX2_CIP_SY
EMX2	CIP_SY	ZSCn117	ZSC_BFS2	ZSC2	EMX2_CIP_SY_ZSCn117	FLZ=FL2		FLZ	FL2	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_BFS2_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT	EMX2_CIP_SY
EMX2	FILL_MX	DVn123	POS_VESSEL	POS2	EMX2_FILL_MX_DVn123					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VESSEL_CMD;	CLOSE			EMX2_FILL_MX
EMX2	FILL_MX	DVn125	POS_SMFL	POS2	EMX2_FILL_MX_DVn125					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_SMFL_CMD;	OPEN			EMX2_FILL_MX
EMX2	FILL_MX	DVn127	POS_DRAIN	POS2	EMX2_FILL_MX_DVn127					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			EMX2_FILL_MX
EMX2	FILL_MX	DVn129	POS_FILL	POS2	EMX2_FILL_MX_DVn129					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILL_CMD;	OPEN			EMX2_FILL_MX
EMX2	FILL_MX	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_FILL_MX_ZSCn111	MX = M1		MX	M1	A(; / L #; / L "dbCONST".SEL.MX.M1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT	EMX2_FILL_MX
EMX2	FILL_MX	ZSCn113	ZSC_FILTER	ZSC2	EMX2_FILL_MX_ZSCn113	MX = M2		MX	M2	A(; / L #; / L "dbCONST".SEL.MX.M2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	EMX2_FILL_MX
EMX2	FILL_MX	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_FILL_MX_ZSCn115	FLZ=FL1		FLZ	FL1	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	EMX2_FILL_MX
EMX2	FILL_MX	ZSCn117	ZSC_BFS2	ZSC2	EMX2_FILL_MX_ZSCn117	FLZ=FL2		FLZ	FL2	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_BFS2_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT	EMX2_FILL_MX
EMX2	FILL_SY	DVn123	POS_VESSEL	POS2	EMX2_FILL_SY_DVn123					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_VESSEL_CMD;	OPEN			EMX2_FILL_SY
EMX2	FILL_SY	DVn125	POS_SMFL	POS2	EMX2_FILL_SY_DVn125					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_SMFL_CMD;	CLOSE			EMX2_FILL_SY
EMX2	FILL_SY	DVn127	POS_DRAIN	POS2	EMX2_FILL_SY_DVn127					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			EMX2_FILL_SY
EMX2	FILL_SY	DVn129	POS_FILL	POS2	EMX2_FILL_SY_DVn129					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILL_CMD;	OPEN			EMX2_FILL_SY
EMX2	FILL_SY	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_FILL_SY_ZSCn111	MX = M1		MX	M1	A(; / L #; / L "dbCONST".SEL.MX.M1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT	EMX2_FILL_SY
EMX2	FILL_SY	ZSCn113	ZSC_FILTER	ZSC2	EMX2_FILL_SY_ZSCn113	MX = M2		MX	M2	A(; / L #; / L "dbCONST".SEL.MX.M2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	EMX2_FILL_SY
EMX2	FILL_SY	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_FILL_SY_ZSCn115	FLZ=FL1		FLZ	FL1	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	EMX2_FILL_SY
EMX2	FILL_SY	ZSCn117	ZSC_BFS2	ZSC2	EMX2_FILL_SY_ZSCn117	FLZ=FL2		FLZ	FL2	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_BFS2_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT	EMX2_FILL_SY
EMX2	FILTER	DVn123	POS_VESSEL	POS2	EMX2_FILTER_DVn123					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_VESSEL_CMD;	OPEN			EMX2_FILTER
EMX2	FILTER	DVn125	POS_SMFL	POS2	EMX2_FILTER_DVn125					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_SMFL_CMD;	OPEN			EMX2_FILTER
EMX2	FILTER	DVn127	POS_DRAIN	POS2	EMX2_FILTER_DVn127					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			EMX2_FILTER
EMX2	FILTER	DVn129	POS_FILL	POS2	EMX2_FILTER_DVn129					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILL_CMD;	CLOSE			EMX2_FILTER
EMX2	FILTER	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_FILTER_ZSCn111	MX = M1		MX	M1	A(; / L #; / L "dbCONST".SEL.MX.M1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT	EMX2_FILTER
EMX2	FILTER	ZSCn113	ZSC_FILTER	ZSC2	EMX2_FILTER_ZSCn113	MX = M2		MX	M2	A(; / L #; / L "dbCONST".SEL.MX.M2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	EMX2_FILTER
EMX2	FILTER	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_FILTER_ZSCn115	FLZ=FL1		FLZ	FL1	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	EMX2_FILTER
EMX2	FILTER	ZSCn117	ZSC_BFS2	ZSC2	EMX2_FILTER_ZSCn117	FLZ=FL2		FLZ	FL2	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_BFS2_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT	EMX2_FILTER
EMX2	SETUP	DVn123	POS_VESSEL	POS2	EMX2_SETUP_DVn123					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VESSEL_CMD;	CLOSE			EMX2_SETUP
EMX2	SETUP	DVn125	POS_SMFL	POS2	EMX2_SETUP_DVn125					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_SMFL_CMD;	CLOSE			EMX2_SETUP
EMX2	SETUP	DVn127	POS_DRAIN	POS2	EMX2_SETUP_DVn127					L "dbCONST".BLK.POS2.CMD.IN; / T #POS_DRAIN_CMD;	IN			EMX2_SETUP
EMX2	SETUP	DVn129	POS_FILL	POS2	EMX2_SETUP_DVn129					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILL_CMD;	CLOSE			EMX2_SETUP
EMX2	SETUP	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_SETUP_ZSCn111	MX = M1		MX	M1	A(; / L #; / L "dbCONST".SEL.MX.M1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.; / T #ZSC_SMFL1_CMD;		EMX2_SETUP
EMX2	SETUP	ZSCn113	ZSC_FILTER	ZSC2	EMX2_SETUP_ZSCn113	MX = M2		MX	M2	A(; / L #; / L "dbCONST".SEL.MX.M2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.; / T #ZSC_FILTER_CMD;		EMX2_SETUP
EMX2	SETUP	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_SETUP_ZSCn115	FLZ=FL1		FLZ	FL1	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	EMX2_SETUP
EMX2	SETUP	ZSCn117	ZSC_BFS2	ZSC2	EMX2_SETUP_ZSCn117	FLZ=FL2		FLZ	FL2	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_BFS2_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT	EMX2_SETUP
EMX2	ISOLATE	DVn123	POS_VESSEL	POS2	EMX2_ISOLATE_DVn123					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_VESSEL_CMD;	CLOSE			EMX2_ISOLATE
EMX2	ISOLATE	DVn125	POS_SMFL	POS2	EMX2_ISOLATE_DVn125					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_SMFL_CMD;	CLOSE			EMX2_ISOLATE
EMX2	ISOLATE	DVn127	POS_DRAIN	POS2	EMX2_ISOLATE_DVn127					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			EMX2_ISOLATE
EMX2	ISOLATE	DVn129	POS_FILL	POS2	EMX2_ISOLATE_DVn129					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILL_CMD;	CLOSE			EMX2_ISOLATE
EMX2	ISOLATE	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_ISOLATE_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX2_ISOLATE
EMX2	ISOLATE	ZSCn113	ZSC_FILTER	ZSC2	EMX2_ISOLATE_ZSCn113					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT			EMX2_ISOLATE
EMX2	ISOLATE	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_ISOLATE_ZSCn115					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT			EMX2_ISOLATE
EMX2	ISOLATE	ZSCn117	ZSC_BFS2	ZSC2	EMX2_ISOLATE_ZSCn117					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT			EMX2_ISOLATE
EMX2	SIP	DVn123	POS_VESSEL	POS2	EMX2_SIP_DVn123					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_VESSEL_CMD;	OPEN			EMX2_SIP
EMX2	SIP	DVn125	POS_SMFL	POS2	EMX2_SIP_DVn125					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_SMFL_CMD;	OPEN			EMX2_SIP
EMX2	SIP	DVn127	POS_DRAIN	POS2	EMX2_SIP_DVn127					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_DRAIN_CMD;	OPEN			EMX2_SIP
EMX2	SIP	DVn129	POS_FILL	POS2	EMX2_SIP_DVn129					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILL_CMD;	OPEN			EMX2_SIP
EMX2	SIP	ZSCn111	ZSC_SMFL1	ZSC2	EMX2_SIP_ZSCn111	MX = M1		MX	M1	A(; / L #; / L "dbCONST".SEL.MX.M1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT	EMX2_SIP
EMX2	SIP	ZSCn113	ZSC_FILTER	ZSC2	EMX2_SIP_ZSCn113	MX = M2		MX	M2	A(; / L #; / L "dbCONST".SEL.MX.M2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN	A(; / L #; / L "dbCONST".SEL.MX.M2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT	EMX2_SIP
EMX2	SIP	ZSCn115	ZSC_CIPSIP	ZSC2	EMX2_SIP_ZSCn115	FLZ=FL1		FLZ	FL1	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_CIPSIP_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL1; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_CIPSIP_CMD;	OUT	EMX2_SIP
EMX2	SIP	ZSCn117	ZSC_BFS2	ZSC2	EMX2_SIP_ZSCn117	FLZ=FL2		FLZ	FL2	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / ==I; / ); / L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_BFS2_CMD;	IN	A(; / L #; / L "dbCONST".SEL.FLZ.FL2; / <>I; / ); / L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_BFS2_CMD;	OUT	EMX2_SIP
EMX4	CIP	BAVSIP	POS_SIP	POS4	EMX4_CIP_BAVSIP					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_SIP_CMD;	CLOSE			EMX4_CIP
EMX4	CIP	BAVCIP	POS_CIP	POS4	EMX4_CIP_BAVCIP					L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_CIP_CMD;	OPEN			EMX4_CIP
EMX4	CIP	TISIP	TI_DRAIN	TI2	EMX4_CIP_TISIP					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_DRAIN_CMD;	ENABLE			EMX4_CIP
EMX4	SIP	TISIP	TI_DRAIN	TI2	EMX4_SIP_TISIP					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_DRAIN_CMD;	ENABLE			EMX4_SIP
EMX4	SIP	BAVSIP	POS_SIP	POS4	EMX4_SIP_BAVSIP					L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_SIP_CMD;	OPEN			EMX4_SIP
EMX4	SIP	BAVCIP	POS_CIP	POS4	EMX4_SIP_BAVCIP					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_CIP_CMD;	CLOSE			EMX4_SIP
EMX4	SIP_PULSE	TISIP	TI_DRAIN	TI2	EMX4_SIP_PULSE_TISIP					L "dbCONST".BLK.TI2.CMD.ENABLE; / T #TI_DRAIN_CMD;	ENABLE			EMX4_SIP_PULSE
EMX4	SIP_PULSE	BAVSIP	POS_SIP	POS4	EMX4_SIP_PULSE_BAVSIP					L "dbCONST".BLK.POS4.CMD.OPEN; / T #POS_SIP_CMD;	OPEN			EMX4_SIP_PULSE
EMX4	SIP_PULSE	BAVCIP	POS_CIP	POS4	EMX4_SIP_PULSE_BAVCIP					L "dbCONST".BLK.POS4.CMD.CLOSE; / T #POS_CIP_CMD;	CLOSE			EMX4_SIP_PULSE
EMX5	FILL	PBn4101	DI_PAUSE	DI2	EMX5_FILL_PBn4101					L "dbCONST".BLK.DI2.CMD.ENABLE; / T #DI_PAUSE_CMD;	ENABLE			EMX5_FILL
EMX6	CIP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_CIP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT			EMX6_CIP
EMX6	CIP	DVn135	POS_DRAIN	POS2	EMX6_CIP_DVn135					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_DRAIN_CMD;	OPEN			EMX6_CIP
EMX6	CIP	DVn137	POS_FILTER	POS2	EMX6_CIP_DVn137					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILTER_CMD;	OPEN			EMX6_CIP
EMX6	CIP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_CIP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT			EMX6_CIP
EMX6	CIP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_CIP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN			EMX6_CIP
EMX6	CIP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_CIP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN			EMX6_CIP
EMX6	CIP_SETUP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_CIP_SETUP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT			#N/A
EMX6	CIP_SETUP	DVn137	POS_FILTER	POS2	EMX6_CIP_SETUP_DVn137					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTER_CMD;	CLOSE			#N/A
EMX6	CIP_SETUP	DVn135	POS_DRAIN	POS2	EMX6_CIP_SETUP_DVn135					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			#N/A
EMX6	CIP_SETUP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_CIP_SETUP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN			#N/A
EMX6	CIP_SETUP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_CIP_SETUP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_SMFL1_CMD;	IN			#N/A
EMX6	CIP_SETUP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_CIP_SETUP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_FILTER_CMD;	OUT			#N/A
EMX6	FILTER	DVn137	POS_FILTER	POS2	EMX6_FILTER_DVn137					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILTER_CMD;	OPEN			EMX6_FILTER
EMX6	FILTER	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_FILTER_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX6_FILTER
EMX6	FILTER	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_FILTER_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX6_FILTER
EMX6	FILTER	ZSCn109	ZSC_FILTER	ZSC2	EMX6_FILTER_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			EMX6_FILTER
EMX6	FILTER	ZSCn109	ZSC_FILTER	ZSC2	EMX6_FILTER_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			EMX6_FILTER
EMX6	FILTER	DVn135	POS_DRAIN	POS2	EMX6_FILTER_DVn135					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			EMX6_FILTER
EMX6	FILTER_BLEED	DVn137	POS_FILTER	POS2	EMX6_FILTER_BLEED_DVn137					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTER_CMD;	CLOSE			EMX6_FILTER_BLEED
EMX6	FILTER_BLEED	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_FILTER_BLEED_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX6_FILTER_BLEED
EMX6	FILTER_BLEED	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_FILTER_BLEED_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX6_FILTER_BLEED
EMX6	FILTER_BLEED	ZSCn109	ZSC_FILTER	ZSC2	EMX6_FILTER_BLEED_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			EMX6_FILTER_BLEED
EMX6	FILTER_BLEED	ZSCn109	ZSC_FILTER	ZSC2	EMX6_FILTER_BLEED_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			EMX6_FILTER_BLEED
EMX6	FILTER_BLEED	DVn135	POS_DRAIN	POS2	EMX6_FILTER_BLEED_DVn135					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			EMX6_FILTER_BLEED
EMX6	SIP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_SIP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX6_SIP
EMX6	SIP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_SIP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			EMX6_SIP
EMX6	SIP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_SIP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			EMX6_SIP
EMX6	SIP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_SIP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			EMX6_SIP
EMX6	SIP	DVn137	POS_FILTER	POS2	EMX6_SIP_DVn137					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_FILTER_CMD;	OPEN			EMX6_SIP
EMX6	SIP	DVn135	POS_DRAIN	POS2	EMX6_SIP_DVn135					L "dbCONST".BLK.POS2.CMD.OPEN; / T #POS_DRAIN_CMD;	OPEN			EMX6_SIP
EMX6	SIP_SETUP	DVn137	POS_FILTER	POS2	EMX6_SIP_SETUP_DVn137					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_FILTER_CMD;	CLOSE			#N/A
EMX6	SIP_SETUP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_SIP_SETUP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			#N/A
EMX6	SIP_SETUP	DVn135	POS_DRAIN	POS2	EMX6_SIP_SETUP_DVn135					L "dbCONST".BLK.POS2.CMD.CLOSE; / T #POS_DRAIN_CMD;	CLOSE			#N/A
EMX6	SIP_SETUP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_SIP_SETUP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			#N/A
EMX6	SIP_SETUP	ZSCn109	ZSC_FILTER	ZSC2	EMX6_SIP_SETUP_ZSCn109					L "dbCONST".BLK.ZSC2.CMD.IN; / T #ZSC_FILTER_CMD;	IN			#N/A
EMX6	SIP_SETUP	ZSCn111	ZSC_SMFL1	ZSC2	EMX6_SIP_SETUP_ZSCn111					L "dbCONST".BLK.ZSC2.CMD.OUT; / T #ZSC_SMFL1_CMD;	OUT			#N/A
FPZ	FILL	EXn101	#N/A	#N/A	FPZ_FILL_EXn101					#N/A	STOP			#N/A
FPZ	FILL	EXn201	#N/A	#N/A	FPZ_FILL_EXn201					#N/A	STOP			#N/A
MX	CIP	EVn004	EMV_VESSEL	EMV1	MX_CIP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			MX_CIP
MX	CIP	ECn002	EMC_WATER	EMC2	MX_CIP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			MX_CIP
MX	CIP	EXn006	EMX_DRAIN	EMX4	MX_CIP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			MX_CIP
MX	CIP	ECn001	EMC_GAS	EMC1	MX_CIP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			MX_CIP
MX	CIP	ECn012	EMC_VACUUM	EMC5	MX_CIP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			MX_CIP
MX	CIP	EGn005	EMG_FILTER	EMG1	MX_CIP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			MX_CIP
MX	CIP	EAn010	EMA_VESSEL	EMA1	MX_CIP_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			MX_CIP
MX	CIP	EVn008	EMV_INLET	EMV2	MX_CIP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			MX_CIP
MX	CIP	EMn009	EMM_VESSEL	EMM1	MX_CIP_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			MX_CIP
MX	CIP	ESn013	EMS_ESTOP	EMS1	MX_CIP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			MX_CIP
MX	FILTER	EAn010	EMA_VESSEL	EMA1	MX_FILTER_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			MX_FILTER
MX	FILTER	ECn012	EMC_VACUUM	EMC5	MX_FILTER_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			MX_FILTER
MX	FILTER	EMn009	EMM_VESSEL	EMM1	MX_FILTER_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			MX_FILTER
MX	FILTER	EGn005	EMG_FILTER	EMG1	MX_FILTER_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			MX_FILTER
MX	FILTER	ESn013	EMS_ESTOP	EMS1	MX_FILTER_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			MX_FILTER
MX	FILTER	EVn004	EMV_VESSEL	EMV1	MX_FILTER_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			MX_FILTER
MX	FILTER	EXn006	EMX_DRAIN	EMX4	MX_FILTER_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			MX_FILTER
MX	FILTER	ECn001	EMC_GAS	EMC1	MX_FILTER_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			MX_FILTER
MX	FILTER	EVn008	EMV_INLET	EMV2	MX_FILTER_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			MX_FILTER
MX	FILTER	ECn002	EMC_WATER	EMC2	MX_FILTER_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			MX_FILTER
MX	MAKE	EGn005	EMG_FILTER	EMG1	MX_MAKE_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			MX_MAKE
MX	MAKE	EMn009	EMM_VESSEL	EMM1	MX_MAKE_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			MX_MAKE
MX	MAKE	EAn010	EMA_VESSEL	EMA1	MX_MAKE_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			MX_MAKE
MX	MAKE	EVn008	EMV_INLET	EMV2	MX_MAKE_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			MX_MAKE
MX	MAKE	ECn012	EMC_VACUUM	EMC5	MX_MAKE_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			MX_MAKE
MX	MAKE	ECn001	EMC_GAS	EMC1	MX_MAKE_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			MX_MAKE
MX	MAKE	ECn002	EMC_WATER	EMC2	MX_MAKE_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			MX_MAKE
MX	MAKE	EXn006	EMX_DRAIN	EMX4	MX_MAKE_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			MX_MAKE
MX	MAKE	EVn004	EMV_VESSEL	EMV1	MX_MAKE_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			MX_MAKE
MX	MAKE	ESn013	EMS_ESTOP	EMS1	MX_MAKE_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			MX_MAKE
MX	CIPSIP_SETUP	EMn009	EMM_VESSEL	EMM1	MX_CIPSIP_SETUP_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	EGn005	EMG_FILTER	EMG1	MX_CIPSIP_SETUP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	EXn006	EMX_DRAIN	EMX4	MX_CIPSIP_SETUP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	ESn013	EMS_ESTOP	EMS1	MX_CIPSIP_SETUP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	EVn008	EMV_INLET	EMV2	MX_CIPSIP_SETUP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	EVn004	EMV_VESSEL	EMV1	MX_CIPSIP_SETUP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	EAn010	EMA_VESSEL	EMA1	MX_CIPSIP_SETUP_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	ECn001	EMC_GAS	EMC1	MX_CIPSIP_SETUP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	ECn002	EMC_WATER	EMC2	MX_CIPSIP_SETUP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			#N/A
MX	CIPSIP_SETUP	ECn012	EMC_VACUUM	EMC5	MX_CIPSIP_SETUP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			#N/A
MX	FILTER_SETUP	EMn009	EMM_VESSEL	EMM1	MX_FILTER_SETUP_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			#N/A
MX	FILTER_SETUP	EGn005	EMG_FILTER	EMG1	MX_FILTER_SETUP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			#N/A
MX	FILTER_SETUP	EXn006	EMX_DRAIN	EMX4	MX_FILTER_SETUP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			#N/A
MX	FILTER_SETUP	ESn013	EMS_ESTOP	EMS1	MX_FILTER_SETUP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			#N/A
MX	FILTER_SETUP	EVn008	EMV_INLET	EMV2	MX_FILTER_SETUP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			#N/A
MX	FILTER_SETUP	EVn004	EMV_VESSEL	EMV1	MX_FILTER_SETUP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			#N/A
MX	FILTER_SETUP	EAn010	EMA_VESSEL	EMA1	MX_FILTER_SETUP_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			#N/A
MX	FILTER_SETUP	ECn001	EMC_GAS	EMC1	MX_FILTER_SETUP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			#N/A
MX	FILTER_SETUP	ECn002	EMC_WATER	EMC2	MX_FILTER_SETUP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			#N/A
MX	FILTER_SETUP	ECn012	EMC_VACUUM	EMC5	MX_FILTER_SETUP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			#N/A
MX	SIP	ECn012	EMC_VACUUM	EMC5	MX_SIP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			MX_SIP
MX	SIP	EVn008	EMV_INLET	EMV2	MX_SIP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			MX_SIP
MX	SIP	EXn006	EMX_DRAIN	EMX4	MX_SIP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			MX_SIP
MX	SIP	ESn013	EMS_ESTOP	EMS1	MX_SIP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			MX_SIP
MX	SIP	EVn004	EMV_VESSEL	EMV1	MX_SIP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			MX_SIP
MX	SIP	EMn009	EMM_VESSEL	EMM1	MX_SIP_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			MX_SIP
MX	SIP	EGn005	EMG_FILTER	EMG1	MX_SIP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			MX_SIP
MX	SIP	EAn010	EMA_VESSEL	EMA1	MX_SIP_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			MX_SIP
MX	SIP	ECn002	EMC_WATER	EMC2	MX_SIP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			MX_SIP
MX	SIP	ECn001	EMC_GAS	EMC1	MX_SIP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			MX_SIP
MX	VACUUM	EAn010	EMA_VESSEL	EMA1	MX_VACUUM_EAn010					L "dbCONST".BLK.EMA1.CMD.STOP; / T #EMA_VESSEL_CMD;	STOP			MX_VACUUM
MX	VACUUM	EMn009	EMM_VESSEL	EMM1	MX_VACUUM_EMn009					L "dbCONST".BLK.EMM1.CMD.STOP; / T #EMM_VESSEL_CMD;	STOP			MX_VACUUM
MX	VACUUM	EXn006	EMX_DRAIN	EMX4	MX_VACUUM_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			MX_VACUUM
MX	VACUUM	ESn013	EMS_ESTOP	EMS1	MX_VACUUM_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			MX_VACUUM
MX	VACUUM	ECn012	EMC_VACUUM	EMC5	MX_VACUUM_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			MX_VACUUM
MX	VACUUM	EGn005	EMG_FILTER	EMG1	MX_VACUUM_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			MX_VACUUM
MX	VACUUM	ECn002	EMC_WATER	EMC2	MX_VACUUM_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			MX_VACUUM
MX	VACUUM	EVn004	EMV_VESSEL	EMV1	MX_VACUUM_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			MX_VACUUM
MX	VACUUM	EVn008	EMV_INLET	EMV2	MX_VACUUM_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			MX_VACUUM
MX	VACUUM	ECn001	EMC_GAS	EMC1	MX_VACUUM_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			MX_VACUUM
PCSTOR	FILL	BFSn	#N/A	#N/A	PCSTOR_FILL_BFSn					#N/A	STOP			PCSTOR_FILL
PCSTOR	FILL	Mn	Mn	MX	PCSTOR_FILL_Mn					L "dbCONST".BLK.MX.CMD.STOP; / T #Mn_CMD;	STOP			PCSTOR_FILL
PCSTOR	FILL	Sn	Sn	SY	PCSTOR_FILL_Sn					L "dbCONST".BLK.SY.CMD.STOP; / T #Sn_CMD;	STOP			PCSTOR_FILL
PCSMS	CIPSIP	Mn	Mn	MX	PCSMS_CIPSIP_Mn					L "dbCONST".BLK.MX.CMD.STOP; / T #Mn_CMD;	STOP			PCSMS_CIPSIP
PCSMS	MAKE	Mn	Mn	MX	PCSMS_MAKE_Mn					L "dbCONST".BLK.MX.CMD.STOP; / T #Mn_CMD;	STOP			PCSMS_MAKE
PCSTOR	CIPSIP	Sn	Sn	SY	PCSTOR_CIPSIP_Sn					L "dbCONST".BLK.SY.CMD.STOP; / T #Sn_CMD;	STOP			PCSTOR_CIPSIP
PCSTOR	CIPSIP	SMFLn	SMFLn	SMFL	PCSTOR_CIPSIP_SMFLn					L "dbCONST".BLK.SMFL.CMD.STOP; / T #SMFLn_CMD;	STOP			PCSTOR_CIPSIP
PCSTOR	FILTER	Sn	Sn	SY	PCSTOR_FILTER_Sn					L "dbCONST".BLK.SY.CMD.STOP; / T #Sn_CMD;	STOP			PCSTOR_FILTER
PCSTOR	FILTER	SMFLn	SMFLn	SMFL	PCSTOR_FILTER_SMFLn					L "dbCONST".BLK.SMFL.CMD.STOP; / T #SMFLn_CMD;	STOP			PCSTOR_FILTER
PCSTOR	FILL_MX	Sn	Sn	SY	PCSTOR_FILL_MX_Sn					L "dbCONST".BLK.SY.CMD.STOP; / T #Sn_CMD;	STOP			PCSTOR_FILL_MX
PCSTOR	FILL_MX	SMFLn	SMFLn	SMFL	PCSTOR_FILL_MX_SMFLn					L "dbCONST".BLK.SMFL.CMD.STOP; / T #SMFLn_CMD;	STOP			PCSTOR_FILL_MX
PCSTOR	FILL_SY	Sn	Sn	SY	PCSTOR_FILL_SY_Sn					L "dbCONST".BLK.SY.CMD.STOP; / T #Sn_CMD;	STOP			PCSTOR_FILL_SY
PCSTOR	FILL_SY	SMFLn	SMFLn	SMFL	PCSTOR_FILL_SY_SMFLn					L "dbCONST".BLK.SMFL.CMD.STOP; / T #SMFLn_CMD;	STOP			PCSTOR_FILL_SY
SMFL	CIP_SETUP	EXn011	EMX_DRAIN	EMX4	SMFL_CIP_SETUP_EXn011					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SMFL_CIP_SETUP
SMFL	CIP_SETUP	EXn007	EMX_TRANSFER	EMX2	SMFL_CIP_SETUP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SMFL_CIP_SETUP
SMFL	CIP	EXn007	EMX_TRANSFER	EMX2	SMFL_CIP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SMFL_CIP
SMFL	CIP	EXn011	EMX_DRAIN	EMX4	SMFL_CIP_EXn011					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SMFL_CIP
SMFL	FILTER	EXn011	EMX_DRAIN	EMX4	SMFL_FILTER_EXn011					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SMFL_FILTER
SMFL	FILTER	EXn007	EMX_TRANSFER	EMX2	SMFL_FILTER_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SMFL_FILTER
SMFL	FILTER_SETUP	EXn011	EMX_DRAIN	EMX4	SMFL_FILTER_SETUP_EXn011					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SMFL_FILTER_SETUP
SMFL	FILTER_SETUP	EXn007	EMX_TRANSFER	EMX2	SMFL_FILTER_SETUP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SMFL_FILTER_SETUP
SMFL	SIP	EXn007	EMX_TRANSFER	EMX2	SMFL_SIP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SMFL_SIP
SMFL	SIP	EXn011	EMX_DRAIN	EMX4	SMFL_SIP_EXn011					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SMFL_SIP
SY	CIP	ECn001	EMC_GAS	EMC1	SY_CIP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			SY_CIP
SY	CIP	ECn002	EMC_WATER	EMC2	SY_CIP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			SY_CIP
SY	CIP	EVn008	EMV_INLET	EMV2	SY_CIP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			SY_CIP
SY	CIP	EGn005	EMG_FILTER	EMG1	SY_CIP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			SY_CIP
SY	CIP	ESn013	EMS_ESTOP	EMS1	SY_CIP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			SY_CIP
SY	CIP	ECn012	EMC_VACUUM	EMC5	SY_CIP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			SY_CIP
SY	CIP	EVn004	EMV_VESSEL	EMV1	SY_CIP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			SY_CIP
SY	CIP	EXn007	EMX_TRANSFER	EMX2	SY_CIP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SY_CIP
SY	CIP	EXn006	EMX_DRAIN	EMX4	SY_CIP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SY_CIP
SY	FILL_MX	ESn013	EMS_ESTOP	EMS1	SY_FILL_MX_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			#N/A
SY	FILL_MX	EXn006	EMX_DRAIN	EMX4	SY_FILL_MX_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			#N/A
SY	FILL_MX	ECn012	EMC_VACUUM	EMC5	SY_FILL_MX_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			#N/A
SY	FILL_MX	EXn007	EMX_TRANSFER	EMX2	SY_FILL_MX_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			#N/A
SY	FILL_MX	ECn002	EMC_WATER	EMC2	SY_FILL_MX_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			#N/A
SY	FILL_MX	ECn001	EMC_GAS	EMC1	SY_FILL_MX_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			#N/A
SY	FILL_MX	EVn008	EMV_INLET	EMV2	SY_FILL_MX_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			#N/A
SY	FILL_MX	EVn004	EMV_VESSEL	EMV1	SY_FILL_MX_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			#N/A
SY	FILL_MX	EGn005	EMG_FILTER	EMG1	SY_FILL_MX_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			#N/A
SY	FILL_SY	ECn001	EMC_GAS	EMC1	SY_FILL_SY_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	EVn004	EMV_VESSEL	EMV1	SY_FILL_SY_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	EVn008	EMV_INLET	EMV2	SY_FILL_SY_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	EXn006	EMX_DRAIN	EMX4	SY_FILL_SY_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	EXn007	EMX_TRANSFER	EMX2	SY_FILL_SY_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	ECn012	EMC_VACUUM	EMC5	SY_FILL_SY_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	ESn013	EMS_ESTOP	EMS1	SY_FILL_SY_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	EGn005	EMG_FILTER	EMG1	SY_FILL_SY_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			SY_FILL_SY
SY	FILL_SY	ECn002	EMC_WATER	EMC2	SY_FILL_SY_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			SY_FILL_SY
SY	FILTER	ESn013	EMS_ESTOP	EMS1	SY_FILTER_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			SY_FILTER
SY	FILTER	ECn012	EMC_VACUUM	EMC5	SY_FILTER_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			SY_FILTER
SY	FILTER	EXn007	EMX_TRANSFER	EMX2	SY_FILTER_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SY_FILTER
SY	FILTER	EXn006	EMX_DRAIN	EMX4	SY_FILTER_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SY_FILTER
SY	FILTER	EVn008	EMV_INLET	EMV2	SY_FILTER_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			SY_FILTER
SY	FILTER	EGn005	EMG_FILTER	EMG1	SY_FILTER_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			SY_FILTER
SY	FILTER	ECn002	EMC_WATER	EMC2	SY_FILTER_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			SY_FILTER
SY	FILTER	EVn004	EMV_VESSEL	EMV1	SY_FILTER_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			SY_FILTER
SY	FILTER	ECn001	EMC_GAS	EMC1	SY_FILTER_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			SY_FILTER
SY	SETUP	EVn004	EMV_VESSEL	EMV1	SY_SETUP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			SY_SETUP
SY	SETUP	ECn012	EMC_VACUUM	EMC5	SY_SETUP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			SY_SETUP
SY	SETUP	EVn008	EMV_INLET	EMV2	SY_SETUP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			SY_SETUP
SY	SETUP	EXn006	EMX_DRAIN	EMX4	SY_SETUP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SY_SETUP
SY	SETUP	EXn007	EMX_TRANSFER	EMX2	SY_SETUP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SY_SETUP
SY	SETUP	EGn005	EMG_FILTER	EMG1	SY_SETUP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			SY_SETUP
SY	SETUP	ECn002	EMC_WATER	EMC2	SY_SETUP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			SY_SETUP
SY	SETUP	ESn013	EMS_ESTOP	EMS1	SY_SETUP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			SY_SETUP
SY	SETUP	ECn001	EMC_GAS	EMC1	SY_SETUP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			SY_SETUP
SY	SIP	EVn008	EMV_INLET	EMV2	SY_SIP_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			SY_SIP
SY	SIP	EGn005	EMG_FILTER	EMG1	SY_SIP_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			SY_SIP
SY	SIP	ECn002	EMC_WATER	EMC2	SY_SIP_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			SY_SIP
SY	SIP	ESn013	EMS_ESTOP	EMS1	SY_SIP_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			SY_SIP
SY	SIP	EXn006	EMX_DRAIN	EMX4	SY_SIP_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SY_SIP
SY	SIP	ECn012	EMC_VACUUM	EMC5	SY_SIP_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			SY_SIP
SY	SIP	EXn007	EMX_TRANSFER	EMX2	SY_SIP_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SY_SIP
SY	SIP	ECn001	EMC_GAS	EMC1	SY_SIP_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			SY_SIP
SY	SIP	EVn004	EMV_VESSEL	EMV1	SY_SIP_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			SY_SIP
SY	VACUUM	EVn008	EMV_INLET	EMV2	SY_VACUUM_EVn008					L "dbCONST".BLK.EMV2.CMD.STOP; / T #EMV_INLET_CMD;	STOP			SY_VACUUM
SY	VACUUM	ESn013	EMS_ESTOP	EMS1	SY_VACUUM_ESn013					L "dbCONST".BLK.EMS1.CMD.STOP; / T #EMS_ESTOP_CMD;	STOP			SY_VACUUM
SY	VACUUM	EXn006	EMX_DRAIN	EMX4	SY_VACUUM_EXn006					L "dbCONST".BLK.EMX4.CMD.STOP; / T #EMX_DRAIN_CMD;	STOP			SY_VACUUM
SY	VACUUM	EGn005	EMG_FILTER	EMG1	SY_VACUUM_EGn005					L "dbCONST".BLK.EMG1.CMD.STOP; / T #EMG_FILTER_CMD;	STOP			SY_VACUUM
SY	VACUUM	ECn002	EMC_WATER	EMC2	SY_VACUUM_ECn002					L "dbCONST".BLK.EMC2.CMD.STOP; / T #EMC_WATER_CMD;	STOP			SY_VACUUM
SY	VACUUM	ECn012	EMC_VACUUM	EMC5	SY_VACUUM_ECn012					L "dbCONST".BLK.EMC5.CMD.STOP; / T #EMC_VACUUM_CMD;	STOP			SY_VACUUM
SY	VACUUM	EXn007	EMX_TRANSFER	EMX2	SY_VACUUM_EXn007					L "dbCONST".BLK.EMX2.CMD.STOP; / T #EMX_TRANSFER_CMD;	STOP			SY_VACUUM
SY	VACUUM	EVn004	EMV_VESSEL	EMV1	SY_VACUUM_EVn004					L "dbCONST".BLK.EMV1.CMD.STOP; / T #EMV_VESSEL_CMD;	STOP			SY_VACUUM
SY	VACUUM	ECn001	EMC_GAS	EMC1	SY_VACUUM_ECn001					L "dbCONST".BLK.EMC1.CMD.STOP; / T #EMC_GAS_CMD;	STOP			SY_VACUUM

## tblClass_IO
Level	ClassID	Class	Mnemonic	Description	Source	DI	DO	AI	AO	PDI	PDO	PAI	PAO	eInstruction	eVerify	eResult	dInstruction	dVerify	dResult
CM	15	DI1	DI	Alarm input	External	1	0	0	0	0	0	0	0
CM	17	HE1	DO	Heating element output	Internal	0	1	0	0	0	0	0	0
CM	17	HE1	FLT	Heater controller fault	Internal	1	0	0	0	0	0	0	0
CM	18	MI1	PV	Load cell measured value	Internal	0	0	0	0	0	0	1	0
CM	19	MOD1	MOD	Valve position in %	External	0	0	0	1	0	0	0	0	HMI : 0% 25% 50% 75% 100%"
CM	20	MOT1	BRK	Motor breaker fault	Internal	1	0	0	0	0	0	0	0
CM	20	MOT1	RLY	Three phase relay alarm	Internal	1	0	0	0	0	0	0	0
CM	20	MOT1	CMD	Motor RUN / STOP command	Internal	0	1	0	0	0	0	0	0
CM	20	MOT1	RUN	Motor Running / Stopped	Internal	1	0	0	0	0	0	0	0
CM	21	PI1	PV	Pressure input	External	0	0	1	0	0	0	0	0	Field: 0% 25% 50% 75% 100%
CM	23	POS1	CMD	Valve OPEN / CLOSE command	External	0	0	0	0	0	1	0	0
CM	24	POS2	CMD	Valve OPEN / CLOSE command	External	0	0	0	0	0	1	0	0	Command valve to OPEN on HMI.	Confirm valve OPENED in Field and on HMI.	Record HMI: Field:	Command valve to CLOSE on HMI.	Confirm valve CLOSED in Field and on HMI.	Record HMI: Field:
CM	24	POS2	ZSC	Valve CLOSED feedback ZSC switch	External	1	0	0	0	0	0	0	0	Confirm valve is CLOSED on HMI.	Confirm valve is CLOSED in Field.	Record HMI: Field:	Confirm valve is OPENED on HMI.	Confirm valve is OPENED in Field.	Record HMI: Field:
CM	25	POS3	CMD	Valve OPEN / CLOSE command	External	0	0	0	0	0	1	0	0	Command valve to OPEN on HMI.	Confirm valve OPENED in Field and on HMI.	Record HMI: Field:	Command valve to CLOSE on HMI.	Confirm valve CLOSED in Field and on HMI.	Record HMI: Field:
CM	25	POS3	ZSO	Valve OPENED feedback ZSO switch	External	1	0	0	0	0	0	0	0	Confirm valve is OPENED on HMI.	Confirm valve is OPENED in Field.	Record HMI: Field:	Confirm valve is CLOSED on HMI.	Confirm valve is CLOSED in Field.	Record HMI: Field:
CM	26	POS4	CMD	Valve OPEN / CLOSE command	External	0	0	0	0	0	1	0	0	Command valve to OPEN on HMI.	Confirm valve OPENED in Field and on HMI.	Record HMI: Field:	Command valve to CLOSE on HMI.	Confirm valve CLOSED in Field and on HMI.	Record HMI: Field:
CM	26	POS4	ZSC	Valve CLOSED feedback ZSC switch	External	1	0	0	0	0	0	0	0	Confirm valve is CLOSED on HMI.	Confirm valve is CLOSED in Field.	Record HMI: Field:	Confirm valve is OPENED on HMI.	Confirm valve is OPENED in Field.	Record HMI: Field:
CM	26	POS4	ZSO	Valve OPENED feedback ZSO switch	External	1	0	0	0	0	0	0	0	Confirm valve is OPENED on HMI.	Confirm valve is OPENED in Field.	Record HMI: Field:	Confirm valve is CLOSED on HMI.	Confirm valve is CLOSED in Field.	Record HMI: Field:
CM	27	SIC1	BRK	Motor breaker fault	Internal	1	0	0	0	0	0	0	0
CM	27	SIC1	CMD	Inverter motor RUN / STOP command	Internal	0	0	0	0	0	1	0	0
CM	27	SIC1	FLP	Pulse counter fault	Internal	1	0	0	0	0	0	0	0
CM	27	SIC1	FLT	Inverter fault	Internal	0	0	0	0	1	0	0	0
CM	27	SIC1	OUT	Inverter speed output value	Internal	0	0	0	0	0	0	0	1	HMI : 0% 25% 50% 75% 100%"
CM	27	SIC1	PV	Motor speed pulse counter measured value	External	0	0	1	0	0	0	0	0
CM	27	SIC1	RLY	Three phase relay alarm	Internal	1	0	0	0	0	0	0	0
CM	27	SIC1	THM	Thermistor module alarm	Internal	1	0	0	0	0	0	0	0
CM	29	TI1	PV	Temperature Measured Value	External	0	0	1	0	0	0	0	0	Field: 0% 25% 50% 75% 100%
CM	30	TI2	PV	Line Temperature Measured Value	External	0	0	1	0	0	0	0	0	Field: 0% 25% 50% 75% 100%
CM	31	ZSC1	DI	Switch input	External	1	0	0	0	0	0	0	0
CM	32	ZSC2	DI	Switch input	External	1	0	0	0	0	0	0	0

## tblFile
File	Level	Generation
dbCONST	PG	File
dbEVENT	PG	File
dbMaster	PG	File
fbBLK	EM	Class
fbBLK	UN	Class
fbBLK	PC	Class
fbDI1	CM	Class
fbHE1	CM	Class
fbHMIReportTrigger	PG	File
fbIL1	IL	Class
fbIL2	IL	Class
fbMI1	CM	Class
fbMOD1	CM	Class
fbMOT1	CM	Class
fbPC1	CM	Class
fbPI1	CM	Class
fbPI2	CM	Class
fbPOSx	CM	Class
fbRunTimer	PG	File
fbSIC1	CM	Class
fbTC1	CM	Class
fbTI1	CM	Class
fbTI2	CM	Class
fbTimeSyncPLC	PG	File
fbZSC1	CM	Class
fbZSC2	CM	Class
fcBLKHygiene	PG	File
fcBLKModeAndCommand	PG	File
fcCallCMs	CM	File
fcCallEMs	EM	File
fcCallILs	IL	File
fcCallPCs	PC	File
fcCallUNs	UN	File
fcHMIBatchReport	PG	File
fcHMIMessages	PG	File
fcHMIPromptMessage	PG	File
fcHMISFCSelect	PG	File
fcHMIStepMessage	PG	File
fcLEDState	PG	File
fcLogRealValue	PG	File
fcLogTimeValue	PG	File
fcSFCCommand	PG	File
fcSfCMode	PG	File
fcTimeHMS	PG	File
fcTimeManagement	PG	File
gPOSTimer	PG	File
gVAR	PG	File
ifbBLK	EM	Class
ifbBLK	UN	Class
ifbBLK	PC	Class
ifbDI1	CM	Class
ifbHE1	CM	Class
ifbHMIPromptMessage	PG	File
ifbHMIStepMessage	PG	File
ifbIL1	IL	Class
ifbIL2	IL	Class
ifbMI1	CM	Class
ifbMOD1	CM	Class
ifbMOT1	CM	Class
ifbPC1	CM	Class
ifbPI1	CM	Class
ifbPOS1	CM	Class
ifbPOS2	CM	Class
ifbPOS4	CM	Class
ifbSFCLogMessage	PG	File
ifbSFCLogReal	PG	File
ifbSFCLogTime	PG	File
ifbSIC1	CM	Class
ifbTC1	CM	Class
ifbTI1	CM	Class
ifbTI2	CM	Class
ifbZSC1	CM	Class
ifbZSC2	CM	Class
ifcBLK	EM	Class
ifcDI1	CM	Class
ifcHE1	CM	Class
ifcHMIAlarms	PG	File
ifcHMISFCControl	PG	File
ifcMI1	CM	Class
ifcMOD1	CM	Class
ifcMOT1	CM	Class
ifcPC1	CM	Class
ifcPI1	CM	Class
ifcPI2	CM	Class
ifcPOSx	CM	Class
ifcSIC1	CM	Class
ifcTC1	CM	Class
ifcTI1	CM	Class
ifcTI2	CM	Class
ifcZSC1	CM	Class
ifcZSC2	CM	Class
obMain	PG	File
udtMaster	PG	File

## tblInterlockCR
Source	Target	Interlock
DV1107	DV1109	A / #INTERLOCK; / A (O / (; / L "idbPOS4".BAV1139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1103.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / ) A (O / (; / L "idbPOS2".DV1105.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1107.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / )
DV1107	DV1115	A / #INTERLOCK; / A (O / (; / L "idbPOS4".BAV1139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1103.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / ) A (O / (; / L "idbPOS2".DV1105.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1107.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / )
ZSC1107	DV1109	O / "idbZSC2".ZSC1103.DI_PV; / O / "idbZSC2".ZSC1107.DI_PV;
ZSC1107	DV1111	O / "idbZSC2".ZSC1103.DI_PV; / O / "idbZSC2".ZSC1107.DI_PV;
ZSC1107	DV1113	O / "idbZSC2".ZSC1105.DI_PV; / O / "idbZSC2".ZSC1107.DI_PV;
ZSC1107	DV1115	O / "idbZSC2".ZSC1105.DI_PV; / O / "idbZSC2".ZSC1107.DI_PV;
DV3101	DV1101	O / (; / L "idbPOS2".DV1109.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1111.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1113.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1115.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".BAV3139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
DV3101	DV1107	O / (; / L "idbPOS2".DV1109.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1111.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1113.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1115.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".BAV3139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
DV3101	DV1111	O / (; / L "idbPOS2".DV1109.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1111.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1113.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1115.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".BAV3139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
DV3101	DV1113	O / (; / L "idbPOS2".DV1109.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1111.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1113.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1115.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".BAV3139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
DV3101	DV1115	O / (; / L "idbPOS2".DV1109.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1111.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV1113.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV1115.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".BAV3139.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3101.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
ZSC3107	DV3109	O / "idbZSC2".ZSC3103.DI_PV; / O / "idbZSC2".ZSC3107.DI_PV;
ZSC3107	DV3111	O / "idbZSC2".ZSC3103.DI_PV; / O / "idbZSC2".ZSC3107.DI_PV;
ZSC3107	DV3113	O / "idbZSC2".ZSC3105.DI_PV; / O / "idbZSC2".ZSC3107.DI_PV;
ZSC3107	DV3115	O / "idbZSC2".ZSC3105.DI_PV; / O / "idbZSC2".ZSC3107.DI_PV;
DV3115	DV3107	O / (; / L "idbPOS2".DV3103.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3105.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3107.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / #INTERLOCK; / O / (; / L "idbPOS2".DV3109.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV3111.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS4".DV3113.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O / (; / L "idbPOS2".DV3115.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
ZSC1115	DV1171	A / "idbZSC2".ZSC1113.DI_PV; / A / "idbZSC2".ZSC1115.DI_PV;
ZSC1115	DV1173	A / "idbZSC2".ZSC1113.DI_PV; / A / "idbZSC2".ZSC1115.DI_PV;
ZSC1115	DV1171	A / "idbZSC2".ZSC1115.DI_PV;
ZSC1111	DV1135	A / "idbZSC2".ZSC1109.DI_PV; / A / "idbZSC2".ZSC1111.DI_PV;
ZSC1111	DV1137	A / "idbZSC2".ZSC1109.DI_PV; / A / "idbZSC2".ZSC1111.DI_PV;
ZSC3111	DV3125	A / "idbZSC2".ZSC3111.DI_PV;
ZSC4113	DV1137	A / "idbZSC2".ZSC3111.DI_PV; / A / "idbZSC2".ZSC4113.DI_PV;
ZSC4113	DV1137	A / "idbZSC2".ZSC3111.DI_PV; / A / "idbZSC2".ZSC3113.DI_PV; / A / "idbZSC2".ZSC4113.DI_PV;
ZSC4113	DV3125	A / "idbZSC2".ZSC3111.DI_PV; / A / "idbZSC2".ZSC3113.DI_PV; / A / "idbZSC2".ZSC4113.DI_PV;
ZSC3117	DV3129	A / "idbZSC2".ZSC3115.DI_PV; / A / "idbZSC2".ZSC3117.DI_PV;
ZSC1101	DV1103	A / "idbZSC1".ZSC1101.DI_PV;
ZSC1101	DV1105	A / "idbZSC1".ZSC1101.DI_PV;
ZSC1101	DV1109	A / "idbZSC1".ZSC1101.DI_PV;
ZSC1101	DV1111	A / "idbZSC1".ZSC1101.DI_PV;
ZSC1101	DV1113	A / "idbZSC1".ZSC1101.DI_PV;
ZSC1101	DV1115	A / "idbZSC1".ZSC1101.DI_PV;
ZSC3101	DV3103	A / "idbZSC1".ZSC3101.DI_PV;
ZSC3101	DV3105	A / "idbZSC1".ZSC3101.DI_PV;
ZSC3101	DV3109	A / "idbZSC1".ZSC3101.DI_PV;
ZSC3101	DV3111	A / "idbZSC1".ZSC3101.DI_PV;
ZSC3101	DV3113	A / "idbZSC1".ZSC3101.DI_PV;
ZSC3101	DV3115	A / "idbZSC1".ZSC3101.DI_PV;
BAV1169	BAV1151	A(O / (; / L "idbPOS4".BAV1167.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O) / (; / L "idbPOS4".BAV1169.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
BAV1169	BAV1153	A(O / (; / L "idbPOS4".BAV1167.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O) / (; / L "idbPOS4".BAV1169.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
BAV1169	TCV1157	A(O / (; / L "idbPOS4".BAV1167.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O) / (; / L "idbPOS4".BAV1169.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
BAV1169	TIC1109	A(O / (; / L "idbPOS4".BAV1167.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / ); / O) / (; / L "idbPOS4".BAV1169.DEV_STATE; / L "dbCONST".CM.POSx_DEV_STATE.OPENED; / ==I; / );
ES1101	AG1101	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1139	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1101	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1103	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1105	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1107	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1109	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1111	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1113	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1115	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	VP1000	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1141	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	HE1101	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	MI1101	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1151	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1153	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1167	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1169	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	TCV1157	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1121	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1117	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1119	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1143	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1145	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1135	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1137	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1147	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	BAV1149	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1171	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	DV1173	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES1101	PC1103	A(O / "idbDI1".ES1100.DI_PV; / O) / "idbDI1".ES1101.DI_PV;
ES3100	BAV3139	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3101	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3103	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3105	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3107	A / "idbDI1".ES3100.DI_PV;
ES3100	PIC3103	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3109	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3111	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3113	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3115	A / "idbDI1".ES3100.DI_PV;
ES3100	BAV3141	A / "idbDI1".ES3100.DI_PV;
ES3100	HE3101	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3121	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3117	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3119	A / "idbDI1".ES3100.DI_PV;
ES3100	BAV3143	A / "idbDI1".ES3100.DI_PV;
ES3100	BAV3145	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3123	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3125	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3127	A / "idbDI1".ES3100.DI_PV;
ES3100	DV3129	A / "idbDI1".ES3100.DI_PV;
PB74101	DV3129	A / "idbDI2".PB74101.DI_PV;
PI1103	BAV1139	A / #INTERLOCK;
PI1103	DV1101	A / #INTERLOCK;
PI1103	DV1103	A / #INTERLOCK;
PI1103	DV1105	A / #INTERLOCK;
PI1103	DV1107	A / #INTERLOCK;
PI1103	DV1109	A / #INTERLOCK;
PI1103	DV1111	A / #INTERLOCK;
PI1103	DV1113	A / #INTERLOCK;
PI1103	DV1115	A / #INTERLOCK;
PI1103	BAV1141	A / #INTERLOCK;
PI1103	HE1101	A / #INTERLOCK;
PI1103	MI1101	A / #INTERLOCK;
PI1103	BAV1151	A / #INTERLOCK;
PI1103	BAV1153	A / #INTERLOCK;
PI1103	BAV1167	A / #INTERLOCK;
PI1103	BAV1169	A / #INTERLOCK;
PI1103	TCV1157	A / #INTERLOCK;
PI1103	TIC1109	A / #INTERLOCK;
PI1103	DV1121	A / #INTERLOCK;
PI1103	DV1117	A / #INTERLOCK;
PI1103	DV1119	A / #INTERLOCK;
PI1103	BAV1143	A / #INTERLOCK;
PI1103	BAV1145	A / #INTERLOCK;
PI1103	DV1135	A / #INTERLOCK;
PI1103	DV1137	A / #INTERLOCK;
PI1103	ZSC1109	A / #INTERLOCK;
PI1103	ZSC1111	A / #INTERLOCK;
PI1103	ZSC1117	A / #INTERLOCK;
PI1103	ZSC1119	A / #INTERLOCK;
PI1103	BAV1147	A / #INTERLOCK;
PI1103	BAV1149	A / #INTERLOCK;
PI1103	DV1171	A / #INTERLOCK;
PI1103	DV1173	A / #INTERLOCK;
PI3103	BAV3139	A / #INTERLOCK;
PI3103	DV3101	A / #INTERLOCK;
PI3103	DV3103	A / #INTERLOCK;
PI3103	DV3105	A / #INTERLOCK;
PI3103	DV3107	A / #INTERLOCK;
PI3103	PIC3103	A / #INTERLOCK;
PI3103	DV3109	A / #INTERLOCK;
PI3103	DV3111	A / #INTERLOCK;
PI3103	DV3113	A / #INTERLOCK;
PI3103	DV3115	A / #INTERLOCK;
PI3103	BAV3141	A / #INTERLOCK;
PI3103	HE3101	A / #INTERLOCK;
PI3103	DV3121	A / #INTERLOCK;
PI3103	DV3117	A / #INTERLOCK;
PI3103	DV3119	A / #INTERLOCK;
PI3103	BAV3143	A / #INTERLOCK;
PI3103	BAV3145	A / #INTERLOCK;
PI3103	DV3123	A / #INTERLOCK;
PI3103	DV3125	A / #INTERLOCK;
PI3103	DV3127	A / #INTERLOCK;
PI3103	DV3129	A / #INTERLOCK;
MI1101	AG1101	A / #INTERLOCK;
MI1101	DV1107	A / #INTERLOCK;
MI1101	DV1109	A / #INTERLOCK;
MI1101	DV1111	A / #INTERLOCK;
MI1101	DV1113	A / #INTERLOCK;
MI1101	DV1115	A / #INTERLOCK;
ASL3000	BAV3139	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3101	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3103	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3105	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3107	A / "idbDI1".ASL3000.DI_PV;
ASL3000	PIC3103	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3109	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3111	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3113	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3115	A / "idbDI1".ASL3000.DI_PV;
ASL3000	BAV3141	A / "idbDI1".ASL3000.DI_PV;
ASL3000	HE3101	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3121	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3117	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3119	A / "idbDI1".ASL3000.DI_PV;
ASL3000	BAV3143	A / "idbDI1".ASL3000.DI_PV;
ASL3000	BAV3145	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3123	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3125	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3127	A / "idbDI1".ASL3000.DI_PV;
ASL3000	DV3129	A / "idbDI1".ASL3000.DI_PV;
ASL1000	AG1101	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1139	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1101	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1103	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1105	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1107	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1109	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1111	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1113	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1115	A / "idbDI1".ASL1000.DI_PV;
ASL1000	VP1000	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1141	A / "idbDI1".ASL1000.DI_PV;
ASL1000	HE1101	A / "idbDI1".ASL1000.DI_PV;
ASL1000	MI1101	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1151	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1153	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1167	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1169	A / "idbDI1".ASL1000.DI_PV;
ASL1000	TCV1157	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1121	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1117	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1119	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1143	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1145	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1135	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1137	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1147	A / "idbDI1".ASL1000.DI_PV;
ASL1000	BAV1149	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1171	A / "idbDI1".ASL1000.DI_PV;
ASL1000	DV1173	A / "idbDI1".ASL1000.DI_PV;
ASL1000	PC1103	A / "idbDI1".ASL1000.DI_PV;

## tblInterlockNCR
Source	Target	Interlock
ZSC1101	AG1101	A / "idbZSC1".ZSC1101.DI_PV;
ZSC1101	DV1107	A / "idbZSC1".ZSC1101.DI_PV;
ZSC3101	DV3107	A / "idbZSC1".ZSC3101.DI_PV;
PI1103	AG1101	A / #INTERLOCK;
MI1101	DV1103	A / #INTERLOCK;
MI1101	DV1105	A / #INTERLOCK;
TI1109	DV1137	A / "idbZSC2".ZSC1113.DI_PV; / A / "idbZSC2".ZSC1109.DI_PV; / A / #INTERLOCK;
ZSC3117	DV3121	A / #INTERLOCK; / A (O / "idbZSC2".ZSC3111.DI_PV; / O) / "idbZSC2".ZSC3113.DI_PV; / A (O / "idbZSC2".ZSC3115.DI_PV; / O) / "idbZSC2".ZSC3117.DI_PV;
ZSC3117	DV3123	A / #INTERLOCK; / A (O / "idbZSC2".ZSC3111.DI_PV; / O) / "idbZSC2".ZSC3113.DI_PV; / A (O / "idbZSC2".ZSC3115.DI_PV; / O) / "idbZSC2".ZSC3117.DI_PV;